## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedules 11a–13
Excluding 11c
| Company Name | Orion New Zealand Limited
| Disclosure Date | 2026-06-09
| AMP Planning Period Start Date (first day) | 2026-04-01
Templates for Schedules 11a–13 excluding 11c
Prepared 19 February 2026.

## TOC
Table of Contents
Information disclosure asset management plan schedules
Schedule | Schedule name
11a | REPORT ON FORECAST CAPITAL EXPENDITURE
11b | REPORT ON FORECAST OPERATIONAL EXPENDITURE
12a | REPORT ON ASSET CONDITION
12b | REPORT ON FORECAST CAPACITY
12c | REPORT ON FORECAST NETWORK DEMAND
12d | REPORT FORECAST INTERRUPTIONS AND DURATION
13 | REPORT ON ASSET MANAGEMENT MATURITY

## S11a.Capex Forecast
Schedule 11a: Report on forecast capital expenditure
sch ref
7 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
8
9 |  | 11a(i): Expenditure on Assets Forecast |  |  |  | $000 (in nominal dollars)
10 |  |  |  |  | Consumer connection | 42936.149 | 39383.345 | 40274.0261 | 41643.4702 | 43093.324 | 45372.6125 | 46385.0175 | 47554.9938 | 48641.0527 | 49828.4578 | 50023.993
11 |  |  |  |  | System growth | 36677.7938 | 16997.9512 | 21254.5842 | 32591.4417 | 36000.8589 | 34879.5809 | 25685.9709 | 16757.7313 | 14228.8876 | 12789.8937 | 11069.4672
12 |  |  |  |  | Asset replacement and renewal | 65343.0855 | 82366.0667 | 99237.891 | 118634.749 | 132184.5712 | 134394.4113 | 130746.6599 | 136484.348 | 140645.2102 | 138480.2834 | 150758.2293
13 |  |  |  |  | Asset relocations | 4142.6082 | 4297.8033 | 4446.354 | 4611.6728 | 4781.7994 | 4958.0007 | 5140.8311 | 5330.5346 | 5527.3752 | 5731.6277 | 5943.5774
14 |  |  |  |  | Reliability, safety and environment:
15 |  |  |  |  | Quality of supply | 3355.23 | 1102.4102 | 1868.1336 | 2028.7297 | 2131.783 | 2238.4576 | 2571.8829 | 2491.3243 | 2118.3724 | 1978.9079 | 1954.0799
16 |  |  |  |  | Legislative and regulatory | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 |  |  |  |  | Other reliability, safety and environment | 6684.622 | 4166.0074 | 1099.583 | 1234.9258 | 1375.8786 | 1522.8758 | 1444.2915 | 1420.3877 | 1455.361 | 1491.2315 | 1528.0235
18 |  |  |  |  | Total reliability, safety and environment | 10039.852 | 5268.4176 | 2967.7166 | 3263.6555 | 3507.6617 | 3761.3334 | 4016.1743 | 3911.712 | 3573.7334 | 3470.1394 | 3482.1034
19 |  |  |  | Expenditure on network assets |  | 159139.4885 | 148313.5837 | 168180.5718 | 200744.9893 | 219568.2151 | 223365.9387 | 211974.6537 | 210039.3197 | 212616.2592 | 210300.402 | 221277.3704
20 |  |  |  | Expenditure on non-network assets |  | 18255.556 | 18710.0105 | 19195.3733 | 13694.9694 | 11771.8287 | 12938.5374 | 10883.0892 | 12980.4176 | 10992.0247 | 13323.2616 | 10810.2041
21 |  |  |  | Expenditure on assets |  | 177395.0445 | 167023.5941 | 187375.9452 | 214439.9587 | 231340.0438 | 236304.4761 | 222857.7429 | 223019.7373 | 223608.2838 | 223623.6636 | 232087.5745
22
23 |  |  | plus |  | Cost of financing | 4814.2891 | 3933.9523 | 4644.4531 | 5110.5632 | 5160.6675 | 4832.6145 | 4179.7159 | 4684.0311 | 4226.2107 | 4299.4382 | 4106.5482
24 |  |  | less |  | Value of capital contributions | 13648.4418 | 13422.8531 | 14646.6747 | 15516.7615 | 16065.6635 | 16626.0639 | 17054.6762 | 17533.8155 | 17994.3353 | 18489.6531 | 18993.454
25 |  |  | plus |  | Value of vested assets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26
27 |  |  |  | Capital expenditure forecast |  | 168560.8918 | 157534.6934 | 177373.7236 | 204033.7605 | 220435.0479 | 224511.0267 | 209982.7826 | 210169.9529 | 209840.1592 | 209433.4488 | 217200.6686
28
29 |  |  |  |  | Assets commissioned | 160200 | 149232.7589 | 166725.8785 | 187754.9531 | 224265.7681 | 226306.8298 | 228924.8266 | 196177.1907 | 222419.3971 | 204093.3185 | 223160.0378
30 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
31
32 | [5 empty] | $000 (in constant prices)
33 |  |  |  |  | Consumer connection | 42936.149 | 38604.6612 | 39307.8261 | 39886.6998 | 40474.6185 | 41786.6953 | 41886.1892 | 42103.2668 | 42220.8506 | 42401.7486 | 41729.6838 | from row 76
34 |  |  |  |  | System growth | 36677.7938 | 16630.2629 | 20579.5146 | 30787.3769 | 33391.2056 | 31577.5779 | 22679.8948 | 14402.3988 | 12028.5548 | 10581.3888 | 8915.4242 | from row 87
35 |  |  |  |  | Asset replacement and renewal | 65343.0855 | 80417.223 | 95459.4855 | 111584.8036 | 121592.6217 | 120776.7238 | 114686.5264 | 116915.6792 | 117680.4025 | 113096.3168 | 120388.7599 | from row 101
36 |  |  |  |  | Asset relocations | 4142.6082 | 4201.4332 | 4261.0935 | 4321.6011 | 4382.9678 | 4445.206 | 4508.3279 | 4572.3461 | 4637.2735 | 4703.1227 | 4769.9071 | from row 113
37 |  |  |  |  | Reliability, safety and environment:
38 |  |  |  |  | Quality of supply | 3355.23 | 1074.2 | 1775.4 | 1881 | 1929 | 1977 | 2217 | 2096 | 1739.4 | 1585.8 | 1528.2 | from row 126
39 |  |  |  |  | Legislative and regulatory | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | from row 139
40 |  |  |  |  | Other reliability, safety and environment | 6684.622 | 4059.401 | 1045 | 1145 | 1245 | 1345 | 1245 | 1195 | 1195 | 1195 | 1195 | from row 154
41 |  |  |  |  | Total reliability, safety and environment | 10039.852 | 5133.601 | 2820.4 | 3026 | 3174 | 3322 | 3462 | 3291 | 2934.4 | 2780.8 | 2723.2
42 |  |  |  | Expenditure on network assets |  | 159139.4885 | 144987.1813 | 162428.3197 | 189606.4814 | 203015.4135 | 201908.2029 | 187222.9383 | 181284.691 | 179501.4814 | 173563.377 | 178526.9749
43 |  |  |  |  | Expenditure on non-network assets | 18255.556 | 18180.387 | 18155.7135 | 12617.0341 | 10569.8266 | 11324.3109 | 9284.6176 | 10793.7184 | 8908.7318 | 10524.2106 | 8322.2064 | from row 182
44 |  |  |  | Expenditure on assets |  | 177395.0445 | 163167.5684 | 180584.0332 | 202223.5155 | 213585.2401 | 213232.5137 | 196507.5559 | 192078.4094 | 188410.2132 | 184087.5876 | 186849.1813
45
46 |  |  |  | Subcomponents of expenditure on assets (where known)
48 |  |  |  |  | Energy efficiency and demand side management, reduction of energy losses
49 |  |  |  |  | Overhead to underground conversion
50 |  |  |  |  | Research and development
52
53 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
54
55 |  |  | Difference between nominal and constant price forecasts |  |  | $000
56 |  |  |  |  | Consumer connection | 0 | 778.6837 | 966.1999 | 1756.7703 | 2618.7055 | 3585.9172 | 4498.8283 | 5451.727 | 6420.2021 | 7426.7092 | 8294.3092
57 |  |  |  |  | System growth | 0 | 367.6883 | 675.0696 | 1804.0648 | 2609.6533 | 3302.003 | 3006.076 | 2355.3325 | 2200.3327 | 2208.5049 | 2154.0431
58 |  |  |  |  | Asset replacement and renewal | 0 | 1948.8437 | 3778.4055 | 7049.9455 | 10591.9495 | 13617.6875 | 16060.1336 | 19568.6688 | 22964.8077 | 25383.9665 | 30369.4695
59 |  |  |  |  | Asset relocations | 0 | 96.3701 | 185.2605 | 290.0718 | 398.8316 | 512.7947 | 632.5032 | 758.1884 | 890.1018 | 1028.505 | 1173.6703
60 |  |  |  |  | Reliability, safety and environment:
61 |  |  |  |  | Quality of supply | 0 | 28.2102 | 92.7336 | 147.7297 | 202.783 | 261.4576 | 354.8829 | 395.3243 | 378.9724 | 393.1079 | 425.8799
62 |  |  |  |  | Legislative and regulatory | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 |  |  |  |  | Other reliability, safety and environment | 0 | 106.6064 | 54.583 | 89.9258 | 130.8786 | 177.8758 | 199.2915 | 225.3877 | 260.361 | 296.2315 | 333.0235
64 |  |  |  |  | Total reliability, safety and environment | 0 | 134.8166 | 147.3166 | 237.6555 | 333.6617 | 439.3334 | 554.1743 | 620.712 | 639.3334 | 689.3394 | 758.9034
65 |  |  |  | Expenditure on network assets |  | 0 | 3326.4024 | 5752.2521 | 11138.5079 | 16552.8016 | 21457.7359 | 24751.7154 | 28754.6288 | 33114.7778 | 36737.025 | 42750.3955
66 |  |  |  |  | Expenditure on non-network assets | 0 | 529.6234 | 1039.6598 | 1077.9353 | 1202.0021 | 1614.2265 | 1598.4716 | 2186.6992 | 2083.2928 | 2799.051 | 2487.9977
67 |  |  |  | Expenditure on assets |  | 0 | 3856.0258 | 6791.9119 | 12216.4432 | 17754.8037 | 23071.9624 | 26350.1871 | 30941.3279 | 35198.0706 | 39536.0761 | 45238.3932
68
69 |  |  | Commentary on options and considerations made in the assessment of forecast expenditure
70 |  |  |  |  | EDBs may provide explanatory comment on the options they have considered (including scenarios used) in assessing forecast expenditure on assets for the current disclosure year and a 10 year planning period in Schedule 15
71
72
73
74 |  | 11a(ii): Consumer Connection |  |  |  | $000 (in constant prices)
75 |  |  |  |  | Consumer types defined by EDB* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
76 |  |  |  |  | Consumer Connection | 42936.149 | CY+1: 38604.6612; CY+2: 39307.8261; CY+3: 39886.6998; CY+4: 40474.6185; CY+5: 41786.6953
77 |  |  |  |  | [EDB consumer type]
78 |  |  |  |  | [EDB consumer type]
79 |  |  |  |  | [EDB consumer type]
80 |  |  |  |  | [EDB consumer type]
81 |  |  |  |  | *include additional rows if needed
82 |  |  |  | Consumer connection expenditure |  | 42936.149 | CY+1: 38604.6612; CY+2: 39307.8261; CY+3: 39886.6998; CY+4: 40474.6185; CY+5: 41786.6953 | to row 33
83 |  |  | less |  | Capital contributions funding consumer connection | 10384.939 | CY+1: 9838.6368; CY+2: 10876.5351; CY+3: 11382.4076; CY+4: 11551.2475; CY+5: 11714.8923
84 |  |  |  | Consumer connection less capital contributions |  | 32551.21 | CY+1: 28766.0244; CY+2: 28431.291; CY+3: 28504.2922; CY+4: 28923.3709; CY+5: 30071.8029
85 |  | 11a(iii): System Growth
86 |  |  |  |  | Subtransmission | 11771.8139 | CY+1: 711.3333; CY+2: 58.5715; CY+3: 458.8104; CY+4: 458.8104; CY+5: 0
87 |  |  |  |  | Zone substations | 15820.309 | CY+1: 4301.1007; CY+2: 4783.2004; CY+3: 8045.7489; CY+4: 11366.8003; CY+5: 5271.176
88 |  |  |  |  | Distribution and LV lines | 567.3511 | CY+1: 739.9489; CY+2: 753.1673; CY+3: 729.2386; CY+4: 733.5336; CY+5: 832.8653
89 |  |  |  |  | Distribution and LV cables | 6183.2966 | CY+1: 8550.0031; CY+2: 11023.9641; CY+3: 14283.4284; CY+4: 14805.1149; CY+5: 18956.4731
90 |  |  |  |  | Distribution substations and transformers | 742.672 | CY+1: 1187.928; CY+2: 2257.444; CY+3: 3815.9121; CY+4: 3813.7281; CY+5: 3810.8343
91 |  |  |  |  | Distribution switchgear | 1592.3511 | CY+1: 1139.9489; CY+2: 1703.1673; CY+3: 3454.2386; CY+4: 2213.2183; CY+5: 2706.2292
92 |  |  |  |  | Other network assets | 0 | CY+1: 0; CY+2: 0; CY+3: 0; CY+4: 0; CY+5: 0
93 |  |  |  | System growth expenditure |  | 36677.7938 | CY+1: 16630.2629; CY+2: 20579.5146; CY+3: 30787.3769; CY+4: 33391.2056; CY+5: 31577.5779 | to row 34
94 |  |  | less |  | Capital contributions funding system growth | 0 | CY+1: 0; CY+2: 0; CY+3: 0; CY+4: 0; CY+5: 0
95 |  |  |  | System growth less capital contributions |  | 36677.7938 | CY+1: 16630.2629; CY+2: 20579.5146; CY+3: 30787.3769; CY+4: 33391.2056; CY+5: 31577.5779
96
97 | [5 empty] | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
98
99 |  | 11a(iv): Asset Replacement and Renewal |  |  |  | $000 (in constant prices)
100 |  |  |  |  | Subtransmission | 13787.5477 | CY+1: 8599.0732; CY+2: 18035.9379; CY+3: 24006.569; CY+4: 23150.5668; CY+5: 22358.9334
101 |  |  |  |  | Zone substations | 5892.5314 | CY+1: 16490.3468; CY+2: 13588.5737; CY+3: 12374.5898; CY+4: 16225.7148; CY+5: 12798.5141
102 |  |  |  |  | Distribution and LV lines | 21653.8365 | CY+1: 25096.233; CY+2: 26336.6774; CY+3: 28288.8619; CY+4: 29376.1104; CY+5: 30113.7032
103 |  |  |  |  | Distribution and LV cables | 2107.6776 | CY+1: 5897.1; CY+2: 8043.8; CY+3: 10149.05; CY+4: 11171.25; CY+5: 11439.15
104 |  |  |  |  | Distribution substations and transformers | 1819.9976 | CY+1: 3093.6809; CY+2: 3609.9231; CY+3: 4225.0917; CY+4: 4147.7758; CY+5: 4564.6776
105 |  |  |  |  | Distribution switchgear | 15412.9149 | CY+1: 13291.4571; CY+2: 17057.6894; CY+3: 22518.4415; CY+4: 26533.222; CY+5: 28254.0293
106 |  |  |  |  | Other network assets | 4668.5798 | CY+1: 7949.332; CY+2: 8786.884; CY+3: 10022.1997; CY+4: 10987.9819; CY+5: 11247.7161
107 |  |  |  | Asset replacement and renewal expenditure |  | 65343.0855 | CY+1: 80417.223; CY+2: 95459.4855; CY+3: 111584.8036; CY+4: 121592.6217; CY+5: 120776.7238 | to row 35
108 |  |  | less |  | Capital contributions funding asset replacement and renewal | 0 | CY+1: 0; CY+2: 0; CY+3: 0; CY+4: 0; CY+5: 0
109 |  |  |  | Asset replacement and renewal less capital contributions |  | 65343.0855 | CY+1: 80417.223; CY+2: 95459.4855; CY+3: 111584.8036; CY+4: 121592.6217; CY+5: 120776.7238
110
111
112
113 |  | 11a(v): Asset Relocations |  |  |  | $000 (in constant prices)
114 |  |  |  |  | Project or programme* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
115 |  |  |  |  | Asset Relocations | 4142.6082 | CY+1: 4201.4332; CY+2: 4261.0935; CY+3: 4321.6011; CY+4: 4382.9678; CY+5: 4445.206
116 |  |  |  |  | [Description of material project or programme]
117 |  |  |  |  | [Description of material project or programme]
118 |  |  |  |  | [Description of material project or programme]
119 |  |  |  |  | [Description of material project or programme]
120 |  |  |  |  | *include additional rows if needed
121 |  |  |  |  | All other project or programmes - asset relocations
122 |  |  |  | Asset relocations expenditure |  | 4142.6082 | CY+1: 4201.4332; CY+2: 4261.0935; CY+3: 4321.6011; CY+4: 4382.9678; CY+5: 4445.206 | to row 36
123 |  |  | less |  | Capital contributions funding asset relocations | 3263.5028 | CY+1: 3309.8445; CY+2: 3356.8443; CY+3: 3404.5115; CY+4: 3452.8556; CY+5: 3501.8861
124 |  |  |  | Asset relocations less capital contributions |  | 879.1054 | CY+1: 891.5886; CY+2: 904.2492; CY+3: 917.0895; CY+4: 930.1122; CY+5: 943.3198
125
126
127
128 |  | 11a(vi): Quality of Supply |  |  |  | $000 (in constant prices)
129 |  |  |  |  | Project or programme* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
130 |  |  |  |  | Quality of Supply | 3355.23 | CY+1: 1074.2; CY+2: 1775.4; CY+3: 1881; CY+4: 1929; CY+5: 1977
131 |  |  |  |  | [Description of material project or programme]
132 |  |  |  |  | [Description of material project or programme]
133 |  |  |  |  | [Description of material project or programme]
134 |  |  |  |  | [Description of material project or programme]
135 |  |  |  |  | *include additional rows if needed
136 |  |  |  |  | All other projects or programmes - quality of supply
137 |  |  |  | Quality of supply expenditure |  | 3355.23 | CY+1: 1074.2; CY+2: 1775.4; CY+3: 1881; CY+4: 1929; CY+5: 1977 | to row 38
138 |  |  | less |  | Capital contributions funding quality of supply | 0 | CY+1: 0; CY+2: 0; CY+3: 0; CY+4: 0; CY+5: 0
139 |  |  |  | Quality of supply less capital contributions |  | 3355.23 | CY+1: 1074.2; CY+2: 1775.4; CY+3: 1881; CY+4: 1929; CY+5: 1977
140
141
142
143 |  | 11a(vii): Legislative and Regulatory |  |  |  | $000 (in constant prices)
144 |  |  |  |  | Project or programme* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
145 |  |  |  |  | [Description of material project or programme]
146 |  |  |  |  | [Description of material project or programme]
147 |  |  |  |  | [Description of material project or programme]
148 |  |  |  |  | [Description of material project or programme]
149 |  |  |  |  | [Description of material project or programme]
150 |  |  |  |  | *include additional rows if needed
151 |  |  |  |  | All other projects or programmes - legislative and regulatory
152 |  |  |  | Legislative and regulatory expenditure |  | 0 | CY+1: 0; CY+2: 0; CY+3: 0; CY+4: 0; CY+5: 0 | to row 39
153 |  |  | less |  | Capital contributions funding legislative and regulatory
154 |  |  |  | Legislative and regulatory less capital contributions |  | 0 | CY+1: 0; CY+2: 0; CY+3: 0; CY+4: 0; CY+5: 0
155
156
157 |  | 11a(viii): Other Reliability, Safety and Environment |  |  |  | $000 (in constant prices)
158 |  |  |  |  | Project or programme* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
159 |  |  |  |  | Other Reliability, Safety and Environment | 6684.622 | CY+1: 4059.401; CY+2: 1045; CY+3: 1145; CY+4: 1245; CY+5: 1345
160 |  |  |  |  | [Description of material project or programme]
161 |  |  |  |  | [Description of material project or programme]
162 |  |  |  |  | [Description of material project or programme]
163 |  |  |  |  | [Description of material project or programme]
164 |  |  |  |  | *include additional rows if needed
165 |  |  |  |  | All other projects or programmes - other reliability, safety and environment
166 |  |  |  | Other reliability, safety and environment expenditure |  | 6684.622 | CY+1: 4059.401; CY+2: 1045; CY+3: 1145; CY+4: 1245; CY+5: 1345 | to row 40
167 |  |  | less |  | Capital contributions funding other reliability, safety and environment
168 |  |  |  | Other reliability, safety and environment less capital contributions |  | 6684.622 | CY+1: 4059.401; CY+2: 1045; CY+3: 1145; CY+4: 1245; CY+5: 1345
169
170 | [5 empty] | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
171
172 |  | 11a(ix): Non-Network Assets
173 |  |  | Routine expenditure |  |  | $000 (in constant prices)
174 |  |  |  |  | Project or programme* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
175 |  |  |  |  | Routine ICT | 9566.556 | CY+1: 13580.687; CY+2: 11045.6135; CY+3: 8554.1341; CY+4: 6992.8266; CY+5: 7573.2109
176 |  |  |  |  | Network Transformation | 856 | CY+1: 1210.7; CY+2: 1405.1; CY+3: 1335.9; CY+4: 1180; CY+5: 1291.1
177 |  |  |  |  | [Description of material project or programme]
178 |  |  |  |  | [Description of material project or programme]
179 |  |  |  |  | [Description of material project or programme]
180 |  |  |  |  | *include additional rows if needed
181 |  |  |  |  | All other projects or programmes - routine expenditure | 7833 | CY+1: 3389; CY+2: 3245; CY+3: 1827; CY+4: 2397; CY+5: 2460
182 |  |  |  | Routine expenditure |  | 18255.556 | CY+1: 18180.387; CY+2: 15695.7135; CY+3: 11717.0341; CY+4: 10569.8266; CY+5: 11324.3109
183 |  |  | Atypical expenditure
184 |  |  |  |  | Project or programme* | Current Year CY | CY+1: CY+1; CY+2: CY+2; CY+3: CY+3; CY+4: CY+4; CY+5: CY+5
185 |  |  |  |  | Head Office Building Extension | 0 | CY+1: 0; CY+2: 2460; CY+3: 900; CY+4: 0; CY+5: 0
186 |  |  |  |  | [Description of material project or programme]
187 |  |  |  |  | [Description of material project or programme]
188 |  |  |  |  | [Description of material project or programme]
189 |  |  |  |  | [Description of material project or programme]
190 |  |  |  |  | *include additional rows if needed
191 |  |  |  |  | All other projects or programmes - atypical expenditure
192 |  |  |  | Atypical expenditure |  | 0 | CY+1: 0; CY+2: 2460; CY+3: 900; CY+4: 0; CY+5: 0
193
194 |  |  | Expenditure on non-network assets |  |  | 18255.556 | CY+1: 18180.387; CY+2: 18155.7135; CY+3: 12617.0341; CY+4: 10569.8266; CY+5: 11324.3109 | to row 43

## S11b.Opex Forecast
[12 empty] | Company Name | Orion New Zealand Limited
[12 empty] | AMP Planning Period | 1 April 2026 - 31 March 2036
Schedule 11b: Report on forecast operational expenditure
7 |  |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
8
9 |  | Operational Expenditure Forecast |  |  | $000 (in nominal dollars)
10 |  |  |  | Service interruptions and emergencies | 12753.9186 | 12917.2092 | 13417.9816 | 13937.7214 | 14475.0059 | 15032.1201 | 15610.757 | 16211.7184 | 16835.8676 | 17484.1015 | 18157.3519
11 |  |  |  | Vegetation management | 5184.1714 | 7314.268 | 8751.799 | 10369.4867 | 11032.2984 | 11554.7298 | 12086.5027 | 12426.8575 | 12805.6845 | 13232.2884 | 13636.9326
12 |  |  |  | Routine and corrective maintenance and inspection | 13574.4002 | 16682.9342 | 19279.1091 | 19907.4188 | 20258.8064 | 21873.5296 | 20876.2318 | 20045.4947 | 20862.7831 | 21530.7607 | 22240.911
13 |  |  |  | Asset replacement and renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 |  |  | Network Opex |  | 31512.4903 | 36914.4115 | 41448.8897 | 44214.6269 | 45766.1107 | 48460.3795 | 48573.4915 | 48684.0706 | 50504.3352 | 52247.1507 | 54035.1956
15 |  |  |  | System operations and network support | 21625.8079 | 22937.1875 | 24605.9908 | 28494.8474 | 29182.8097 | 29970.3917 | 29958.0734 | 30386.8052 | 30915.0825 | 31471.2335 | 32352.7821
16 |  |  |  | Business support | 37170.4149 | 42519.3498 | 48331.325 | 50134.6605 | 52332.1718 | 54448.8547 | 54776.096 | 56033.8595 | 57505.1106 | 58987.3566 | 60938.5067
17 |  |  |  | Non-network solutions provided by a related party or third party | 0 | 0 | 0 | 406.4477 | 945.5755 | 223.1965 | 1000.5134 | 279.3594 | 507.5847 | 741.0297 | 311.8855
18 |  |  | Non-network opex |  | 58796.2228 | 65456.5373 | 72937.3158 | 79035.9556 | 82460.5569 | 84642.443 | 85734.6827 | 86700.0241 | 88927.7778 | 91199.6199 | 93603.1744
19 |  |  | Operational expenditure |  | 90308.7131 | 102370.9487 | 114386.2054 | 123250.5826 | 128226.6676 | 133102.8225 | 134308.1742 | 135384.0947 | 139432.113 | 143446.7706 | 147638.37
20 |  |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
21
22 |  |  |  |  | $000 (in constant prices)
23 |  |  |  | Service interruptions and emergencies | 12753.9186 | 12607.4544 | 12786.4803 | 12968.0483 | 13152.1946 | 13338.9558 | 13528.3689 | 13720.4718 | 13915.3025 | 14112.8998 | 14313.3029
24 |  |  |  | Vegetation management | 5184.1714 | 7132.3704 | 8330.5773 | 9638.4031 | 10017.2903 | 10250.2682 | 10475.2061 | 10522.2093 | 10593.2519 | 10693.9839 | 10767.0441
25 |  |  |  | Routine and corrective maintenance and inspection | 13574.4002 | 16302.9303 | 18416.9781 | 18590.7732 | 18497.981 | 19529.0916 | 18224.8878 | 17111.0588 | 17413.1546 | 17571.4438 | 17747.666
26 |  |  |  | Asset replacement and renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 |  |  | Network Opex |  | 31512.4903 | 36042.7551 | 39534.0357 | 41197.2246 | 41667.4658 | 43118.3156 | 42228.4629 | 41353.7399 | 41921.7091 | 42378.3275 | 42828.0131
28 |  |  |  | System operations and network support | 21625.8079 | 22449.3031 | 23575.8171 | 26726.871 | 26799.6621 | 26948.594 | 26375.2618 | 26194.2286 | 26093.1859 | 26007.8848 | 26177.9659
29 |  |  |  | Business support | 37170.4149 | 41550.6969 | 46188.5589 | 46865.5049 | 47865.5024 | 48733.0405 | 47973.6244 | 48021.5262 | 48223.9835 | 48404.3087 | 48930.8266
30 |  |  |  | Non-network solutions provided by a related party or third party | 0 | 0 | 0 | 379.9443 | 864.8685 | 199.7663 | 876.2627 | 239.4135 | 425.6622 | 608.08 | 250.4298
31 |  |  | Non-network opex |  | 58796.2228 | 64000 | 69764.376 | 73972.3201 | 75530.0331 | 75881.4008 | 75225.1489 | 74455.1683 | 74742.8317 | 75020.2735 | 75359.2222
32 |  |  | Operational expenditure |  | 90308.7131 | 100042.7551 | 109298.4117 | 115169.5447 | 117197.4989 | 118999.7164 | 117453.6117 | 115808.9081 | 116664.5408 | 117398.601 | 118187.2353
33 |  | Subcomponents of operational expenditure (where known)
35
36 |  |  |  | Energy efficiency and demand side management, reduction of energy losses
37 |  |  |  | Direct billing*
38 |  |  |  | Research and Development
39 |  |  |  | Insurance
41 | * Direct billing expenditure by suppliers that direct bill the majority of their consumers
42
43 |  |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
44
45 |  | Difference between nominal and real forecasts |  |  | $000
46 |  |  |  | Service interruptions and emergencies | 0 | 309.7548 | 631.5013 | 969.6731 | 1322.8113 | 1693.1643 | 2082.3881 | 2491.2466 | 2920.5651 | 3371.2018 | 3844.049
47 |  |  |  | Vegetation management | 0 | 181.8976 | 421.2217 | 731.0837 | 1015.0081 | 1304.4616 | 1611.2966 | 1904.6482 | 2212.4326 | 2538.3045 | 2869.8885
48 |  |  |  | Routine and corrective maintenance and inspection | 0 | 380.0039 | 862.131 | 1316.6456 | 1760.8254 | 2344.4381 | 2651.3439 | 2934.4359 | 3449.6285 | 3959.3169 | 4493.245
49 |  |  |  | Asset replacement and renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 |  |  | Network Opex |  | 0 | 871.6563 | 1914.854 | 3017.4023 | 4098.6449 | 5342.064 | 6345.0286 | 7330.3308 | 8582.6262 | 9868.8232 | 11207.1825
51 |  |  |  | System operations and network support | 0 | 487.8844 | 1030.1736 | 1767.9765 | 2383.1475 | 3021.7977 | 3582.8116 | 4192.5766 | 4821.8966 | 5463.3487 | 6174.8163
52 |  |  |  | Business support | 0 | 968.6529 | 2142.7661 | 3269.1556 | 4466.6693 | 5715.8142 | 6802.4716 | 8012.3333 | 9281.1271 | 10583.0479 | 12007.6802
53 |  |  |  | Non-network solutions provided by a related party or third party | 0 | 0 | 0 | 26.5034 | 80.707 | 23.4302 | 124.2506 | 39.9459 | 81.9224 | 132.9497 | 61.4557
54 |  |  | Non-network opex |  | 0 | 1456.5373 | 3172.9397 | 5063.6355 | 6930.5239 | 8761.0422 | 10509.5338 | 12244.8558 | 14184.9461 | 16179.3464 | 18243.9522
55 |  |  | Operational expenditure |  | 0 | 2328.1936 | 5087.7937 | 8081.0379 | 11029.1687 | 14103.1061 | 16854.5625 | 19575.1865 | 22767.5722 | 26048.1696 | 29451.1347
56

## S12a.Asset Condition
[9 empty] | Company Name | Orion New Zealand Limited
[9 empty] | AMP Planning Period | 1 April 2026 - 31 March 2036
SCHEDULE 12a: REPORT ON ASSET CONDITION
sch ref
7 | [5 empty] | Asset condition at start of planning period (percentage of units by grade)
8
9 |  | Voltage | Asset category | Asset class | Units | H1 | H2 | H3 | H4 | H5 | Grade unknown | Data accuracy (1–4) | % of asset forecast to be replaced in next 5 years
10 |  | All | Overhead Line | Concrete poles / steel structure | No. | 1.129% | 0.9411% | 5.131% | 7.201% | 85.6% | 0% | 3 | 3.125%
11 |  | All | Overhead Line | Wood poles | No. | 1.848% | 3.209% | 11.67% | 18.28% | 64.99% | 0% | 3 | 7.607%
12 |  | All | Overhead Line | Other pole types | No. | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
13 |  | HV | Subtransmission Line | Subtransmission OH up to 66kV conductor | km | 1.823% | 0.5686% | 3.037% | 4.795% | 89.78% | 0% | 3 | 1.472%
14 |  | HV | Subtransmission Line | Subtransmission OH 110kV+ conductor | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
15 |  | HV | Subtransmission Cable | Subtransmission UG up to 66kV (XLPE) | km | 0.04929% | 0.1586% | 2.432% | 9.721% | 87.64% | 0% | 3 | 0%
16 |  | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Oil pressurised) | km | 13.14% | 18.43% | 68.43% | 0% | 0% | 0% | 3 | 58.51%
17 |  | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Gas pressurised) | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
18 |  | HV | Subtransmission Cable | Subtransmission UG up to 66kV (PILC) | km | 3.244% | 7.814% | 42.29% | 35.18% | 11.48% | 0% | 3 | 0%
19 |  | HV | Subtransmission Cable | Subtransmission UG 110kV+ (XLPE) | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
20 |  | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Oil pressurised) | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
21 |  | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Gas Pressurised) | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
22 |  | HV | Subtransmission Cable | Subtransmission UG 110kV+ (PILC) | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
23 |  | HV | Subtransmission Cable | Subtransmission submarine cable | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
24 |  | HV | Zone substation Buildings | Zone substations up to 66kV | No. | 2.381% | 9.524% | 38.1% | 29.76% | 20.24% | 0% | 3 | 33.33%
25 |  | HV | Zone substation Buildings | Zone substations 110kV+ | No. | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
26 |  | HV | Zone substation switchgear | 22/33kV CB (Indoor) | No. | 0% | 0% | 0% | 56.25% | 43.75% | 0% | 3 | 0%
27 |  | HV | Zone substation switchgear | 22/33kV CB (Outdoor) | No. | 34.62% | 7.692% | 34.62% | 0% | 23.08% | 0% | 3 | 61.54%
28 |  | HV | Zone substation switchgear | 33kV Switch (Ground Mounted) | No. | 0% | 0% | 0% | 0% | 100% | 0% | N/A | 0%
29 |  | HV | Zone substation switchgear | 33kV Switch (Pole Mounted) | No. | 27.66% | 0.8511% | 10.21% | 5.532% | 55.74% | 0% | 3 | 34.89%
30 |  | HV | Zone substation switchgear | 33kV RMU | No. | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
31 |  | HV | Zone substation switchgear | 50/66/110kV CB (Indoor) | No. | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
32 |  | HV | Zone substation switchgear | 50/66/110kV CB (Outdoor) | No. | 6.667% | 0% | 0.7407% | 32.59% | 60% | 0% | 3 | 8.889%
33 |  | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (ground mounted) | No. | 8.029% | 0.8759% | 14.45% | 37.81% | 38.83% | 0% | 3 | 3.65%
34 |  | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (pole mounted) | No. | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
35
36 | [5 empty] | Asset condition at start of planning period (percentage of units by grade)
37
38 |  | Voltage | Asset category | Asset class | Units | H1 | H2 | H3 | H4 | H5 | Grade unknown | Data accuracy (1–4) | % of asset forecast to be replaced in next 5 years
39 |  | HV | Zone Substation Transformer | Zone Substation Transformers | No. | 0.062% | 0.1499% | 1.125% | 3.279% | 95.38% | 0% | 2 | 1.704%
40 |  | HV | Distribution Line | Distribution OH Open Wire Conductor | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
41 |  | HV | Distribution Line | Distribution OH Aerial Cable Conductor | km | 0.7195% | 1.49% | 7.885% | 14.34% | 75.56% | 0% | 2 | 6.358%
42 |  | HV | Distribution Line | SWER conductor | km | 0.07335% | 0.1553% | 1.194% | 5.069% | 93.51% | 0% | 3 | 0.4127%
43 |  | HV | Distribution Cable | Distribution UG XLPE or PVC | km | 0.9007% | 1.843% | 8.868% | 15.67% | 72.72% | 0% | 3 | 3.368%
44 |  | HV | Distribution Cable | Distribution UG PILC | km | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
45 |  | HV | Distribution Cable | Distribution Submarine Cable | km | 0.001547% | 0.006579% | 0.2913% | 3.619% | 96.08% | 0% | 3 | 0%
46 |  | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (pole mounted) - reclosers and sectionalisers | No. | 5.279% | 10.41% | 32.58% | 22.78% | 28.96% | 0% | 3 | 12.2%
47 |  | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (Indoor) | No. | 0.9455% | 1.914% | 9.154% | 20.01% | 67.98% | 0% | 3 | 3.671%
48 |  | HV | Distribution switchgear | 3.3/6.6/11/22kV Switches and fuses (pole mounted) | No. | 0.721% | 1.682% | 9.694% | 12.78% | 75.13% | 0% | 3 | 3.058%
49 |  | HV | Distribution switchgear | 3.3/6.6/11/22kV Switch (ground mounted) - except RMU | No. | 71.07% | 0% | 0% | 1.523% | 27.41% | 0% | 3 | 35.53%
50 |  | HV | Distribution switchgear | 3.3/6.6/11/22kV RMU | No. | 0.857% | 1.741% | 8.229% | 11.85% | 77.32% | 0% | 3 | 4.474%
51 |  | HV | Distribution Transformer | Pole Mounted Transformer | No. | 0.2945% | 0.7199% | 4.516% | 8.704% | 85.77% | 0% | 3 | 1.865%
52 |  | HV | Distribution Transformer | Ground Mounted Transformer | No. | 33.67% | 19.87% | 27.9% | 15.88% | 2.683% | 0% | 3 | 27.53%
53 |  | HV | Distribution Transformer | Voltage regulators | No. | 0.5499% | 1.197% | 6.804% | 11.67% | 79.78% | 0% | 3 | 2.597%
54 |  | HV | Distribution Substations | Ground Mounted Substation Housing | No. | 0.2604% | 0.6164% | 3.966% | 7.924% | 87.23% | 0% | 2 | 1.713%
55 |  | LV | LV Line | LV OH Conductor | km | 0.008392% | 0.02383% | 0.3385% | 2.12% | 97.51% | 0% | 3 | 0.08612%
56 |  | LV | LV Cable | LV UG Cable | km | 0.678% | 1.542% | 8.757% | 15.19% | 73.83% | 0% | 2 | 3.884%
57 |  | LV | LV Streetlighting | LV OH/UG Streetlight circuit | km | 0.4313% | 6.848% | 13.7% | 47.93% | 31.09% | 0% | 2 | 0.4313%
58 |  | LV | Connections | OH/UG consumer service connections | No. | 13.15% | 3.554% | 23.03% | 23.66% | 36.61% | 0% | 3 | 11.3%
59 |  | All | Protection | Protection relays (electromechanical, solid state and numeric) | No. | 12.06% | 6.505% | 64.87% | 13.96% | 2.602% | 0% | 3 | 24.9%
60 |  | All | SCADA and communications | SCADA and communications equipment operating as a single system | Lot | 8.395% | 14.99% | 42.96% | 27.29% | 6.372% | 0% | 3 | 22.43%
61 |  | All | Capacitor Banks | Capacitors including controls | No. | 13.33% | 0% | 48.89% | 22.22% | 15.56% | 0% | 3 | 15.56%
62 |  | All | Load Control | Centralised plant | Lot | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
63 |  | All | Load Control | Relays | No. | 0% | 0% | 0% | 0% | 0% | 0% | N/A | 0%
64 |  | All | Civils | Cable Tunnels | km | [6 empty] | [Select one]

## S12b.Capacity Forecast
[20 empty] | Company Name | Orion NZ Limited
[20 empty] | AMP Planning Period | 1 April 2026 - 31 March 2036
SCHEDULE 12b: REPORT ON FORECAST CAPACITY
7 | 12b(i): System Growth - Zone Substations
8 | Existing Zone Substations | Current peak load (MVA) | Current peak load period | Installed operating capacity (MVA) | Current security of supply classification (type) | Current constraint type | Current available capacity (MVA) | Peak load period +5 yrs | Available capacity +5 yrs (MVA) | Security of supply classification +5 yrs (type) | Peak load period +10 yrs | Min. available capacity +10 yrs (MVA) | Max. available capacity +10 yrs (MVA) | Security of supply classification +10 yrs (type) | Forecast constraint type | Year of any forecast constraint | Constraint primary cause | Constraint solution type | Constraint solution progress | Temporary constraint solution remaining lifespan | Explanation
9 | ADDINGTON #1 | 18.9701 | Winter | 37.4 | N-1 | No constraint | 18.4299 | Winter | 15.7154 | N-1 | Winter | 11.5652 | 15.2108 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
10 | ADDINGTON #2 | 22.5422 | Winter | 30 | N-1 | No constraint | 7.4578 | Winter | 5.285 | N-1 | Winter | 0.60804 | 4.6047 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
11 | ANNAT | 3.7915 | Summer | 8 | N-1 switched | Security | 4.2085 | Summer | 4.4029 | N-1 switched | Summer | 4.4465 | 4.3386 | N-1 switched | Security | 1 | Distribution back-up circuit capacity | Other non-traditional solution | Solution confirmed | Not applicable | Project in FY27 to install STATCOM to restore switched N-1 capability
12 | ARMAGH | 22.2092 | Winter | 38.8 | N-1 | No constraint | 16.5908 | Winter | 15.052 | N-1 | Winter | 10.8613 | 14.0357 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
13 | BANKSIDE | 3.8454 | Summer | 9.4 | N-1 switched | No constraint | 5.5546 | Summer | 5.9058 | N-1 switched | Summer | 5.8718 | 5.8665 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
14 | BARNETT PARK | 9.7296 | Winter | 15 | N-1 switched | No constraint | 5.2704 | Winter | 5.7379 | N-1 switched | Winter | 3.2447 | 4.6173 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
15 | BELFAST | 12.7239 | Winter | 15 | N-1 switched | No constraint | 2.2761 | Winter | 2.4816 | N-1 switched | Winter | -2.2009 | 1.7605 | N-1 switched | Security | 7 | Other | Undecided | No active planning | Not applicable | Transformer capacity is 40MVA but operational limit is 15MVA due to switched N-1. Loading to be monitored and offload opportunities to be assessed
16 | BROMLEY | 38.6895 | Winter | 47.6 | N-1 | No constraint | 8.9105 | Winter | 5.0169 | N-1 | Winter | -1.3477 | 3.5661 | N-1 | Security | 9 | Zone substation transformer | Undecided | No active planning | Not applicable | Loading actively monitored to determine solution type required
17 | BROOKSIDE | 8.9038 | Summer | 10 | N-1 switched | No constraint | 1.0962 | Summer | 1.3735 | N-1 switched | Summer | 1.0769 | 1.1799 | N-1 switched | Security | 10+ | Not applicable | Not required | Not applicable | Not applicable
18 | DALLINGTON | 24.3175 | Winter | 38.8 | N-1 | Security | 14.4825 | Winter | 13.2872 | N-1 | Winter | 8.5048 | 12.4 | N-1 | Security | 1 | Subtransmission circuit | Not required | No active planning | Not applicable | Security breach due to site loading requiring full N-1 but only switchable N-1 available. Rapid switchable restoration available for 66kV circuit fault so currently uneconomic to resolve security gap
19 | DARFIELD | 5.9667 | Winter | 9.6 | N-1 switched | No constraint | 3.6333 | Winter | 4.2472 | N-1 switched | Winter | 2.4733 | 3.5435 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
20 | DIAMOND HARBOUR | 3.2898 | Winter | 8.7 | N-1 switched | No constraint | 5.4102 | Winter | 5.7227 | N-1 switched | Winter | 5.3122 | 5.2603 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
21 | DUNSANDEL | 19.2907 | Summer | 23.8 | N-1 | No constraint | 4.5093 | Summer | 4.0594 | N-1 | Summer | -7.0271 | 1.8091 | N-1 | Security | 6 | Zone substation transformer | Undecided | No active planning | Not applicable | Large customer connection causing forecast potential security breach. Timing and scope to be determined of solution to be determined by customer capacity need
22 | DUVAUCHELLE | 4.3026 | Winter | 8.3 | N-1 switched | No constraint | 3.9974 | Winter | 4.0442 | N-1 switched | Winter | 3.7782 | 3.6108 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
23 | FENDALTON | 36.7491 | Winter | 42 | N-1 | No constraint | 5.2509 | Winter | 3.9369 | N-1 | Winter | -0.7623 | 1.877 | N-1 | No constraint | 10+ | Zone substation transformer | Divert load to alternative substation | No active planning | Not applicable | Marginal forecast security breach. Opportunities for 11kV load transfer to be assessed.
24 | GREENDALE | 6.8622 | Summer | 10 | N-1 switched | No constraint | 3.1378 | Summer | 3.3254 | N-1 switched | Summer | 3.1677 | 3.1682 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
25 | HALSWELL | 22.9997 | Winter | 23.8 | N-1 | No constraint | 0.80032 | Winter | 0.91639 | N-1 | Winter | -1.1504 | -1.9504 | N-1 | Security | 7 | Zone substation transformer | Undecided | Planning stage | 1 - 3 years | Investigation and economic analysis required for forecast security breach to determine network and non-network option feasibility.
26 | HAWTHORNDEN | 33.2498 | Winter | 38.8 | N-1 | No constraint | 5.5502 | Winter | 1.6162 | N-1 | Winter | -2.8718 | -2.2018 | N-1 | Security | 6 | Zone substation transformer | Divert load to alternative substation | Planning stage | Not applicable | Minor project to create post-contingency switching and/or reinforcement options being assessed
27 | HEATHCOTE | 28.8837 | Winter | 38.8 | N-1 | No constraint | 9.9163 | Winter | 7.9146 | N-1 | Winter | -8.7523 | 6.5077 | N-1 | Security | 7 | Zone substation transformer | Undecided | Planning stage | Not applicable | Forecast security breach driven by major customer growth. Timing and solution(s) to be confirmed
28 | HIGHFIELD | 9.1485 | Summer | 10 | N-1 switched | No constraint | 0.85153 | Summer | 0.51052 | N-1 switched | Summer | -0.68393 | 0.0081253 | N-1 switched | Capacity | 7 | Zone substation transformer | Network upgrade | Solution confirmed | Not applicable | Capacity breach resolved through Malvern industrial growth major project
29 | HILLS RD | 7.9863 | Summer | 9.9 | N-1 switched | No constraint | 1.9137 | Summer | 2.1829 | N-1 switched | Summer | 2.1072 | 1.9015 | N-1 switched | Security | 6 | Distribution back-up circuit capacity | Undecided | Planning stage | Not applicable | Forecast security breach with lower voltage threshold exceeded at network extremities during subtranmission or transformer contingencies at peak load times. Load growth being monitored and modelled for contingent outages. Options being developed.
30 | HOON HAY | 31.5731 | Winter | 38.8 | N-1 | No constraint | 7.2269 | Winter | 8.8049 | N-1 | Winter | 5.0813 | 6.8239 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
31 | HORNBY | 15.4008 | Winter | 22.8 | N-1 | No constraint | 7.3992 | Winter | 6.9302 | N-1 | Winter | 3.8407 | 6.0226 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
32 | HORORATA | 9.2119 | Summer | 9.6 | N-1 switched | No constraint | 0.38809 | Summer | 1.1472 | N-1 switched | Summer | 1.181 | 1.127 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
33 | ILAM | 14.1528 | Winter | 15 | N-1 | Security | 0.84719 | Winter | 6 | N-1 | Winter | 3 | 5 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
34 | KILLINCHY | 9.9391 | Summer | 10 | N-1 switched | No constraint | 0.060852 | Summer | 0.75627 | N-1 switched | Summer | -0.90276 | 0.17016 | N-1 switched | Capacity | 7 | Zone substation transformer | Network upgrade | Solution confirmed | Not applicable | Business case developed for a forecast capacity upgrade in FY36. Operational capacity to be lifted to 15MVA
35 | KIMBERLEY | 15.5278 | Summer | 23.8 | N-1 | No constraint | 8.2722 | Summer | 9.1111 | N-1 | Summer | 8.7904 | 8.9079 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
36 | LANCASTER | 23.2411 | Winter | 47.6 | N-1 | Security | 24.3589 | Winter | 20.7664 | N-1 | Winter | 15.8921 | 19.836 | N-1 | Security | 1 | Subtransmission circuit | Network upgrade | Solution confirmed | Not applicable | Rapid switchable N-1 available for a 66kV circuit fault. N-1 to be provided in FY28
37 | LARCOMB | 24.5269 | Winter | 23.8 | N-1 | Security | -0.72693 | Winter | -1.4267 | N-1 | Winter | -10.9195 | -3.4429 | N-1 | Security | 3 | Zone substation transformer | Divert load to alternative substation | Solution confirmed | Not applicable | Security breach to be resolved with new Rolleston (Burnham) zone substation
38 | LINCOLN | 11.2917 | Winter | 15 | N-1 switched | No constraint | 3.7083 | Winter | 1.57 | N-1 switched | Winter | -2.3212 | -1.576 | N-1 | Security | 1 | Zone substation transformer | Network upgrade | Solution confirmed | Not applicable | Forecast load exceeds 15MVA requiring N-1. Security breach to be resolved with replacement new Greenpark zone substation
39 | LITTLE RIVER | 1.6448 | Summer | 2.8 | N-1 | No constraint | 1.1552 | Summer | 2.0903 | N-1 switched | Summer | 2.0049 | 2.0075 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
40 | MCFADDENS | 35.3713 | Winter | 38.8 | N-1 | No constraint | 3.4287 | Winter | 2.5337 | N-1 | Winter | -4.4187 | 2.0059 | N-1 | Security | 7 | Zone substation transformer | Divert load to alternative substation | No active planning | Not applicable | If required, load transfer options to be assessed
41 | MIDDLETON | 29.576 | Winter | 45.7 | N-1 | No constraint | 16.124 | Winter | 9.8509 | N-1 | Winter | 2.0831 | 8.977 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
42 | MILTON | 36.7015 | Winter | 42 | N-1 | No constraint | 5.2985 | Winter | 4.1664 | N-1 | Winter | -1.5445 | 2.8263 | N-1 | Security | 9 | Zone substation transformer | Undecided | No active planning | Not applicable | Loading actively monitored to determine solution type required
43 | MOFFETT ST | 19.3479 | Summer | 22.8 | N-1 | No constraint | 3.4521 | Summer | 2.3844 | N-1 | Summer | -1.0296 | 1.6163 | N-1 | Security | 9 | Zone substation transformer | Divert load to alternative substation | Solution confirmed | Not applicable | Forecast security breach to be resolved through the transfer of load to the proposed Templeton ZS as part of the Templeton commercial growth business case
44 | MOTUKARARA | 3.4327 | Summer | 15 | N-1 switched | No constraint | 11.5673 | Summer | 12 | N-1 | Summer | 11 | 11 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
45 | OXFORD-TUAM | 21.9708 | Winter | 38.8 | N-1 | No constraint | 16.8292 | Winter | 14.2033 | N-1 | Winter | 9.3849 | 13.3948 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
46 | PAPANUI | 36.0284 | Winter | 50.4 | N-1 | No constraint | 14.3716 | Winter | 12.6563 | N-1 | Winter | 7.7314 | 10.4601 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
47 | PREBBLETON | 9.161 | Winter | 15 | N-1 switched | No constraint | 5.839 | Winter | 4.9999 | N-1 switched | Winter | 2.7806 | 4.9187 | N-1 switched | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
48 | RAWHITI | 34.1961 | Winter | 38.8 | N-1 | Security | 4.6039 | Winter | 5.9776 | N-1 | Winter | 3.6888 | 4.1294 | N-1 | Security | 10+ | Subtransmission circuit | Not required | Not applicable | Not applicable | Rapid switchable N-1 available for a 66kV circuit fault. Not currently economical to provide full N-1
49 | ROLLESTON | 14.0417 | Winter | 15 | N-1 switched | No constraint | 0.95826 | Winter | -0.54585 | N-1 switched | Winter | -5.9032 | -5.3273 | N-1 switched | Security | 1 | Zone substation transformer | Network upgrade | Implementation stage | Not applicable | Security breach to be resolved with new Rolleston (Burnham) zone substation replacement. Operational capacity will be lifted to 24MVA providing N-1
50 | SHANDS RD | 16.8457 | Winter | 22.9 | N-1 | No constraint | 6.0543 | Winter | 5.1815 | N-1 | Winter | 1.9129 | 4.5421 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
51 | SOCKBURN | 24.6317 | Winter | 36.5 | N-1 | No constraint | 11.8683 | Winter | 9.2173 | N-1 | Winter | 4.0699 | 7.9022 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
52 | SPRINGSTON | 12.3523 | Winter | 23.8 | N-1 | No constraint | 11.4477 | Winter | 6.2544 | N-1 | Winter | 2.9572 | 4.9481 | N-1 | No constraint | 10+ | Not applicable | Not required | Not applicable | Not applicable
53 | TE PIRITA | 9.3866 | Summer | 10 | N-1 switched | No constraint | 0.61338 | Summer | 0.71978 | N-1 switched | Summer | -0.11374 | 0.36729 | N-1 switched | Security | 6 | Distribution back-up circuit capacity | Undecided | No active planning | Not applicable | Forecast security breach with lower voltage threshold exceeded at network extremities during subtranmission or transformer contingencies at peak load times. Load growth being monitored and modelled for contingent outages.
54 | WAIMAKARIRI | 23.6538 | Winter | 47.6 | N-1 | Security | 23.9462 | Winter | 21.8751 | N-1 switched | Winter | 17.0889 | 20.8712 | N-1 | Security | 10+ | Subtransmission circuit | Not required | No active planning | Not applicable | Security breach due to site loading requiring full N-1 but only switchable N-1 available. Rapid switchable restoration available for 66kV circuit fault so currently uneconomic to resolve security gap
55 | WEEDONS | 16.3343 | Winter | 23.8 | N-1 | No constraint | 7.4657 | Winter | 4.3195 | N-1 | Winter | -1.1185 | 3.023 | N-1 | Security | 9 | Zone substation transformer | Divert load to alternative substation | Implementation stage | Not applicable | Security breach forecast due to distribution network configuration. Loading to be reduced with new Rolleston ZS project
56 | ¹ Extend table as necessary to disclose all capacity and constraint information by each zone substation

## S12c.Demand Forecast
[8 empty] | Company Name | Orion New Zealand Limited
[8 empty] | AMP Planning Period | 1 April 2026 - 31 March 2036
Schedule 12c: Report on forecast network demand
7 |  | 12c(i): Consumer Connections
8 |  |  |  | Number of ICPs connected during year by consumer type
9
10 | [5 empty] | Number of connections
11 |  |  |  |  | Consumer types defined by EDB* | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
12 |  |  |  |  | Streetlighting | 16 | 5 | 5 | 5 | 5 | 5
13 |  |  |  |  | General | 6700 | 6034 | 6107.08 | 6197.597 | 6289.528 | 6378.631
14 |  |  |  |  | Irrigation | 5 | 5 | 5 | 5 | 5 | 5
15 |  |  |  |  | Major Customer | 20 | 20 | 20 | 20 | 20 | 20
16 |  |  |  |  | Large Capacity | 3 | 3 | 3 | 3 | 3 | 3
17 |  |  |  |  | Connections total | 6744 | 6067 | 6140.08 | 6230.597 | 6322.528 | 6411.631
18 |  |  |  |  | *include additional rows if needed
19
20
21
22 |  |  | Distributed generation |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
23 |  |  |  |  | Number of connections made in year | 1532 | 1176.2277 | 1190.894 | 1144.7757 | 1029.1748 | 907.494
24 |  |  |  |  | Capacity of distributed generation installed in year (MVA) | 12.9 | 16.0207 | 156.1764 | 6.0302 | 5.5301 | 4.9877
25 |  | 12c(ii): System Demand
26 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
27 |  |  | Maximum coincident system demand (MW)
28 |  |  |  |  | GXP demand | 697.442 | 718.4116 | 739.5337 | 756.4962 | 780.0631 | 806.8747
29 |  |  | plus |  | Distributed generation output at HV and above |  |  | 0.14 | 1.9 | 1.9 | 2.9
30 |  |  |  | Maximum coincident system demand |  | 697.442 | 718.4116 | 739.6737 | 758.3962 | 781.9631 | 809.7747
31 |  |  | less |  | Net transfers to (from) other EDBs at HV and above
32 |  |  |  | Demand on system for supply to consumers' connection points |  | 697.442 | 718.4116 | 739.6737 | 758.3962 | 781.9631 | 809.7747
33 |  |  | Electricity volumes carried (GWh)
34 |  |  |  |  | Electricity supplied from GXPs | 3632 | 3846.6908 | 4033.9573 | 4197.5455 | 4444.7361 | 4662.415
35 |  |  | less |  | Electricity exports to GXPs
36 |  |  | plus |  | Electricity supplied from distributed generation | 82 | 67.1571 | 73.1574 | 77.7431 | 80.5246 | 83.4189
37 |  |  | less |  | Net electricity supplied to (from) other EDBs
38 |  |  |  | Electricity entering system for supply to ICPs |  | 3714 | 3913.8479 | 4107.1148 | 4275.2886 | 4525.2607 | 4745.8339
39 |  |  | less |  | Total energy delivered to ICPs | 3474.933 | 3680.3395 | 3859.5076 | 4016.0214 | 4252.5221 | 4460.7874
40 |  |  |  | Losses |  | 239.067 | 233.5084 | 247.6072 | 259.2672 | 272.7386 | 285.0465
41
42 |  |  |  | Load factor |  | 60.79% | 62.19% | 63.39% | 64.35% | 66.06% | 66.9%
43 |  |  |  | Loss ratio |  | 6.437% | 5.966% | 6.029% | 6.064% | 6.027% | 6.006%

## S12d.Reliability Forecast
[5 empty] | Company Name | Orion New Zealand Limited
[5 empty] | AMP Planning Period | 1/04/2026 - 31 March 2036
[5 empty] | Network / Sub-network Name | Total Network
SCHEDULE 12d: REPORT FORECAST INTERRUPTIONS AND DURATION
sch ref
8 |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
9
10 | SAIDI
11 |  | Class B (planned interruptions on the network) | 29.55 | 26.31 | 26.31 | 26.31 | 26.31 | 26.31
12 |  | Class C (unplanned interruptions on the network) | 73.61 | 51.81 | 51.81 | 51.81 | 51.81 | 51.81
13 | SAIFI
14 |  | Class B (planned interruptions on the network) | 0.1231 | 0.087 | 0.087 | 0.087 | 0.087 | 0.087
15 |  | Class C (unplanned interruptions on the network) | 0.57 | 0.621 | 0.621 | 0.621 | 0.621 | 0.621

## S13.AMMAT
[6 empty] | Company Name | Orion New Zealand Limited | [6 empty] | Company Name | Orion New Zealand Limited
[6 empty] | AMP Planning Period | 1 April 2026 - 31 March 2036 | [6 empty] | AMP Planning Period | 1 April 2026 - 31 March 2036
[6 empty] | Asset Management Standard Applied | PAS55 | [6 empty] | Asset Management Standard Applied | PAS55
Schedule 13: Report on asset management maturity | [8 empty] | Schedule 13: Report on asset management maturity (cont'd)
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
3 | Asset management policy | To what extent has an asset management policy been documented, authorised and communicated? | 3.5 | Asset Management Policy is available and has recently been updated. AM Policy is aligned with the latest Statement of Intent document. Orion has a well-structured Asset Management Policy document. It covers off all the required focus areas and is aligned with current Orion business strategies and objectives. The AM Policy document is reference consistently in many asset related documents. The policy document is aligned with current business objectives, and explicitly seeks alignment with ISO 55000 and ISO 31000. Upon review against the CPP preparatory materials, no fundamental policy-level weaknesses are apparent. Policy documentation is sound with clear articulation of asset management principles. While organisational restructuring affects implementation, this does not diminish the quality of the policy framework itself. |  | Widely used AM practice standards require an organisation to document, authorise and communicate its asset management policy (eg, as required in PAS 55 para 4.2 i). A key pre-requisite of any robust policy is that the organisation's top management must be seen to endorse and fully support it. Also vital to the effective implementation of the policy, is to tell the appropriate people of its content and their obligations under it. Where an organisation outsources some of its asset-related activities, then these people and their organisations must equally be made aware of the policy's content. Also, there may be other stakeholders, such as regulatory authorities and shareholders who should be made aware of it. | Top management. The management team that has overall responsibility for asset management. | The organisation's asset management policy, its organisational strategic plan, documents indicating how the asset management policy was based upon the needs of the organisation and evidence of communication. | 3 | Asset management policy | To what extent has an asset management policy been documented, authorised and communicated? | The organisation does not have a documented asset management policy. | The organisation has an asset management policy, but it has not been authorised by top management, or it is not influencing the management of the assets. | The organisation has an asset management policy, which has been authorised by top management, but it has had limited circulation. It may be in use to influence development of strategy and planning but its effect is limited. | The asset management policy is authorised by top management, is widely and effectively communicated to all relevant employees and stakeholders, and used to make these persons aware of their asset related obligations. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
10 | Asset management strategy | What has the organisation done to ensure that its asset management strategy is consistent with other appropriate organisational policies and strategies, and the needs of stakeholders? | 2.5 | Orion have recently created a separate SAMP document. It is well structured and aligned with the AM Policy. The SAMP's interaction with other AM processes is well illustrated in the document. This is a document which many of Orion’s key staff and stakeholders will soon be able to reference as required, to gain insights into Orion’s AMS. The SAMP represents strategic direction setting rather than demonstrated strategic management capability. The CPP-driven development timeline indicates this is foundational work awaiting validation through implementation cycles. Currently, only network development and lifecycle strategies are directly linked to the SAMP. Other organisational strategies and policies in ICT, Network Transformation, and business support (people) are not yet connected to the SAMP, representing gaps in demonstrating consistency across Orion. Although the AMP provides a solid foundation, and key staff and stakeholders can reference it for insights into the AMS, the incomplete linkages mean Orion cannot demonstrate that the AM Strategy is fully consistent with all appropriate policies and strategies as Level 3 requires. They recognise this gap, and will be working to establish the remaining linkages via first developing and documenting the AMS Scope. |  | In setting an organisation's asset management strategy, it is important that it is consistent with any other policies and strategies that the organisation has and has taken into account the requirements of relevant stakeholders. This question examines to what extent the asset management strategy is consistent with other organisational policies and strategies (eg, as required by PAS 55 para 4.3.1 b) and has taken account of stakeholder requirements as required by PAS 55 para 4.3.1 c). Generally, this will take into account the same polices, strategies and stakeholder requirements as covered in drafting the asset management policy but at a greater level of detail. | Top management. The organisation's strategic planning team. The management team that has overall responsibility for asset management. | The organisation's asset management strategy document and other related organisational policies and strategies. Other than the organisation's strategic plan, these could include those relating to health and safety, environmental, etc. Results of stakeholder consultation. | 10 | Asset management strategy | What has the organisation done to ensure that its asset management strategy is consistent with other appropriate organisational policies and strategies, and the needs of stakeholders? | The organisation has not considered the need to ensure that its asset management strategy is appropriately aligned with the organisation's other organisational policies and strategies or with stakeholder requirements. OR The organisation does not have an asset management strategy. | The need to align the asset management strategy with other organisational policies and strategies as well as stakeholder requirements is understood and work has started to identify the linkages or to incorporate them in the drafting of asset management strategy. | Some of the linkages between the long-term asset management strategy and other organisational policies, strategies and stakeholder requirements are defined but the work is fairly well advanced but still incomplete. | All linkages are in place and evidence is available to demonstrate that, where appropriate, the organisation's asset management strategy is consistent with its other organisational policies and strategies. The organisation has also identified and considered the requirements of relevant stakeholders. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
11 | Asset management strategy | In what way does the organisation's asset management strategy take account of the lifecycle of the assets, asset types and asset systems over which the organisation has stewardship? | 3 | Orion's new SAMP is structured well and highlights strategies and key objectives for all of their asset classes. It provides insights into how assets will be managed throughout their lifecycle. We also note that while Orion report on Non-Network lifecycle strategies in their AMP regulatory disclosure, they do not have specific, and documented, Asset Class Strategies for all non-network asset types. |  | Good asset stewardship is the hallmark of an organisation compliant with widely used AM standards. A key component of this is the need to take account of the lifecycle of the assets, asset types and asset systems. (For example, this requirement is recognised in 4.3.1 d) of PAS 55). This question explores what an organisation has done to take lifecycle into account in its asset management strategy. | Top management. People in the organisation with expert knowledge of the assets, asset types, asset systems and their associated life-cycles. The management team that has overall responsibility for asset management. Those responsible for developing and adopting methods and processes used in asset management | The organisation's documented asset management strategy and supporting working documents. | 11 | Asset management strategy | In what way does the organisation's asset management strategy take account of the lifecycle of the assets, asset types and asset systems over which the organisation has stewardship? | The organisation has not considered the need to ensure that its asset management strategy is produced with due regard to the lifecycle of the assets, asset types or asset systems that it manages. OR The organisation does not have an asset management strategy. | The need is understood, and the organisation is drafting its asset management strategy to address the lifecycle of its assets, asset types and asset systems. | The long-term asset management strategy takes account of the lifecycle of some, but not all, of its assets, asset types and asset systems. | The asset management strategy takes account of the lifecycle of all of its assets, asset types and asset systems. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
26 | Asset management plan(s) | How does the organisation establish and document its asset management plan(s) across the life cycle activities of its assets and asset systems? | 3.25 | Orion have comprehensive Asset Management Plans (AMPs). The latest AMP 2025 is an update AMP as is approved by the Commerce Commission. The last full AMP was published in 2024 While the AMP 2024 is comprehensive, the necessity of a significant value CPP application to address deferred maintenance warrants consideration of the scoring of this section. An AMP that has allowed accumulation of renewal deferrals requiring exceptional funding mechanisms does not support "Optimising" level scoring. The acknowledged need for significant AMP 2026 revision further supports this adjustment. |  | The asset management strategy need to be translated into practical plan(s) so that all parties know how the objectives will be achieved. The development of plan(s) will need to identify the specific tasks and activities required to optimize costs, risks and performance of the assets and/or asset system(s), when they are to be carried out and the resources required. | The management team with overall responsibility for the asset management system. Operations, maintenance and engineering managers. | The organisation's asset management plan(s). | 26 | Asset management plan(s) | How does the organisation establish and document its asset management plan(s) across the life cycle activities of its assets and asset systems? | The organisation does not have an identifiable asset management plan(s) covering asset systems and critical assets. | The organisation has asset management plan(s) but they are not aligned with the asset management strategy and objectives and do not take into consideration the full asset life cycle (including asset creation, acquisition, enhancement, utilisation, maintenance decommissioning and disposal). | The organisation is in the process of putting in place comprehensive, documented asset management plan(s) that cover all life cycle activities, clearly aligned to asset management objectives and the asset management strategy. | Asset management plan(s) are established, documented, implemented and maintained for asset systems and critical assets to achieve the asset management strategy and asset management objectives across all life cycle phases. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
27 | Asset management plan(s) | How has the organisation communicated its plan(s) to all relevant parties to a level of detail appropriate to the receiver's role in their delivery? | 3.25 | The Orion AMP's are published on their web page for all to access. They also undertake specific consultation both before and post final AMP publication with key Stakeholders. There is always room for improvement here. |  | Plans will be ineffective unless they are communicated to all those, including contracted suppliers and those who undertake enabling function(s). The plan(s) need to be communicated in a way that is relevant to those who need to use them. | The management team with overall responsibility for the asset management system. Delivery functions and suppliers. | Distribution lists for plan(s). Documents derived from plan(s) which detail the receivers role in plan delivery. Evidence of communication. | 27 | Asset management plan(s) | How has the organisation communicated its plan(s) to all relevant parties to a level of detail appropriate to the receiver's role in their delivery? | The organisation does not have plan(s) or their distribution is limited to the authors. | The plan(s) are communicated to some of those responsible for delivery of the plan(s). OR Communicated to those responsible for delivery is either irregular or ad-hoc. | The plan(s) are communicated to most of those responsible for delivery but there are weaknesses in identifying relevant parties resulting in incomplete or inappropriate communication. The organisation recognises improvement is needed as is working towards resolution. | The plan(s) are communicated to all relevant employees, stakeholders and contracted service providers to a level of detail appropriate to their participation or business interests in the delivery of the plan(s) and there is confirmation that they are being used effectively. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
29 | Asset management plan(s) | How are designated responsibilities for delivery of asset plan actions documented? | 3.25 | Yes the specific responsibility for the development of the next Amps documented for the Network Strategy and Investment Manager role. As Orion now have a specific asset management team, many of this team will provide focused input into the next AMP for 2026. The establishment of the AM Team surpasses the requirements of PAS 55. Orion have established excellent processes for the updating on both Full and Update AMPs as required by the regulator. |  | The implementation of asset management plan(s) relies on (1) actions being clearly identified, (2) an owner allocated and (3) that owner having sufficient delegated responsibility and authority to carry out the work required. It also requires alignment of actions across the organisation. This question explores how well the plan(s) set out responsibility for delivery of asset plan actions. | The management team with overall responsibility for the asset management system. Operations, maintenance and engineering managers. If appropriate, the performance management team. | The organisation's asset management plan(s). Documentation defining roles and responsibilities of individuals and organisational departments. | 29 | Asset management plan(s) | How are designated responsibilities for delivery of asset plan actions documented? | The organisation has not documented responsibilities for delivery of asset plan actions. | Asset management plan(s) inconsistently document responsibilities for delivery of plan actions and activities and/or responsibilities and authorities for implementation inadequate and/or delegation level inadequate to ensure effective delivery and/or contain misalignments with organisational accountability. | Asset management plan(s) consistently document responsibilities for the delivery of actions but responsibility/authority levels are inappropriate/ inadequate, and/or there are misalignments within the organisation. | Asset management plan(s) consistently document responsibilities for the delivery actions and there is adequate detail to enable delivery of actions. Designated responsibility and authority for achievement of asset plan actions is appropriate. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
31 | Asset management plan(s) | What has the organisation done to ensure that appropriate arrangements are made available for the efficient and cost effective implementation of the plan(s)? (Note this is about resources and enabling support) | 2.5 | Orion actively updates it's vast array of asset class and portfolio documentation and process instructions. These link directly with the latest AMP. The AMP is developed after all of the higher hierarchy documents (Business Plans, SOI and AM Policy etc.) have been updated and approved by top management. The AMP brings all of that strategy and direction together to provide even more detail and specific direction. As well as reporting on past asset performance. While Orion have arrangements in place for AMP implementation, these arrangements do not yet meet the level 3 standard for efficient & cost-effective implementation. Their current process is resource-intensive, requiring excessive iterations through forecasts, reviews, and approvals, meaning that implementation is not efficient nor cost-effective. Changes to functional policies, standards, processes and AMIS drive changes to the AMP, rather than the AMP driving necessary organisational changes; this reactive approach, means Orion cannot claim to "fully cover all requirements". Orion acknowledge these weaknesses and are actively working to resolve them through a comprehensive review of how AMP2026 and future AMPs will be produced. |  | It is essential that the plan(s) are realistic and can be implemented, which requires appropriate resources to be available and enabling mechanisms in place. This question explores how well this is achieved. The plan(s) not only need to consider the resources directly required and timescales, but also the enabling activities, including for example, training requirements, supply chain capability and procurement timescales. | The management team with overall responsibility for the asset management system. Operations, maintenance and engineering managers. If appropriate, the performance management team. If appropriate, the performance management team. Where appropriate the procurement team and service providers working on the organisation's asset-related activities. | The organisation's asset management plan(s). Documented processes and procedures for the delivery of the asset management plan. | 31 | Asset management plan(s) | What has the organisation done to ensure that appropriate arrangements are made available for the efficient and cost effective implementation of the plan(s)? (Note this is about resources and enabling support) | The organisation has not considered the arrangements needed for the effective implementation of plan(s). | The organisation recognises the need to ensure appropriate arrangements are in place for implementation of asset management plan(s) and is in the process of determining an appropriate approach for achieving this. | The organisation has arrangements in place for the implementation of asset management plan(s) but the arrangements are not yet adequately efficient and/or effective. The organisation is working to resolve existing weaknesses. | The organisation's arrangements fully cover all the requirements for the efficient and cost effective implementation of asset management plan(s) and realistically address the resources and timescales required, and any changes needed to functional policies, standards, processes and the asset management information system. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
33 | Contingency planning | What plan(s) and procedure(s) does the organisation have for identifying and responding to incidents and emergency situations and ensuring continuity of critical asset management activities? | 3.25 | Orion are very focused on effective contingency planning, due to the nature of their business and as a result of the past events such as the Christchurch earthquakes and other natural events in the area. Orion has continued to improve their resilience to business interruption by targeting three main focus areas and ensuring that they have the right systems, people and processes in place to quickly and effectively respond to all types of events. They have also recently completed Resilience Management Maturity Assessment Tool (RMMAT) process which benchmarked them highly against peer EDB's. We have previously recognised strong contingency planning capability due to Canterbury earthquakes experience (RMMAT score 3.01 exceeds sector average 2.55). Upon review of CPP documentation, "Building network resilience to reduce major outage risk" is identified as a core driver, specifically citing high earthquake risk requiring substantial investment to strengthen the 66kV network. The requirement for significant capital investment to close resilience gaps warrants reconsideration of the "Optimising" score. Historical contingency planning excellence is acknowledged. However, the CPP explicitly identifies continuing resilience vulnerabilities requiring substantial investment (66kV network strengthening). Outstanding resilience gaps requiring a significant investment programme indicate remaining development opportunities rather than fully optimised capability. Orion have not updated our contingency plans over the last two years They have only just started looking at infrastructure resilience, taking into account risks and consequences of climate impact. |  | Widely used AM practice standards require that an organisation has plan(s) to identify and respond to emergency situations. Emergency plan(s) should outline the actions to be taken to respond to specified emergency situations and ensure continuity of critical asset management activities including the communication to, and involvement of, external agencies. This question assesses if, and how well, these plan(s) triggered, implemented and resolved in the event of an incident. The plan(s) should be appropriate to the level of risk as determined by the organisation's risk assessment methodology. It is also a requirement that relevant personnel are competent and trained. | The manager with responsibility for developing emergency plan(s). The organisation's risk assessment team. People with designated duties within the plan(s) and procedure(s) for dealing with incidents and emergency situations. | The organisation's plan(s) and procedure(s) for dealing with emergencies. The organisation's risk assessments and risk registers. | 33 | Contingency planning | What plan(s) and procedure(s) does the organisation have for identifying and responding to incidents and emergency situations and ensuring continuity of critical asset management activities? | The organisation has not considered the need to establish plan(s) and procedure(s) to identify and respond to incidents and emergency situations. | The organisation has some ad-hoc arrangements to deal with incidents and emergency situations, but these have been developed on a reactive basis in response to specific events that have occurred in the past. | Most credible incidents and emergency situations are identified. Either appropriate plan(s) and procedure(s) are incomplete for critical activities or they are inadequate. Training/ external alignment may be incomplete. | Appropriate emergency plan(s) and procedure(s) are in place to respond to credible incidents and manage continuity of critical asset management activities consistent with policies and asset management objectives. Training and external agency alignment is in place. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
37 | Structure, authority and responsibilities | What has the organisation done to appoint member(s) of its management team to be responsible for ensuring that the organisation's assets deliver the requirements of the asset management strategy, objectives and plan(s)? | 3 | The Orion AMP 2024 – section 2.10 Asset management roles and accountabilities, provides details on how the organisation’s governance/management structure is arranged. SAMP provides updated information. The org chart has changed within the last 9 months with the creation of a new Asset Management team which mostly incorporates the old Future Network team, but with some adjustments and realignment of people. |  | In order to ensure that the organisation's assets and asset systems deliver the requirements of the asset management policy, strategy and objectives responsibilities need to be allocated to appropriate people who have the necessary authority to fulfil their responsibilities. (This question, relates to the organisation's assets eg, para b), s 4.4.1 of PAS 55, making it therefore distinct from the requirement contained in para a), s 4.4.1 of PAS 55). | Top management. People with management responsibility for the delivery of asset management policy, strategy, objectives and plan(s). People working on asset-related activities. | Evidence that managers with responsibility for the delivery of asset management policy, strategy, objectives and plan(s) have been appointed and have assumed their responsibilities. Evidence may include the organisation's documents relating to its asset management system, organisational charts, job descriptions of post-holders, annual targets/objectives and personal development plan(s) of post-holders as appropriate. | 37 | Structure, authority and responsibilities | What has the organisation done to appoint member(s) of its management team to be responsible for ensuring that the organisation's assets deliver the requirements of the asset management strategy, objectives and plan(s)? | Top management has not considered the need to appoint a person or persons to ensure that the organisation's assets deliver the requirements of the asset management strategy, objectives and plan(s). | Top management understands the need to appoint a person or persons to ensure that the organisation's assets deliver the requirements of the asset management strategy, objectives and plan(s). | Top management has appointed an appropriate people to ensure the assets deliver the requirements of the asset management strategy, objectives and plan(s) but their areas of responsibility are not fully defined and/or they have insufficient delegated authority to fully execute their responsibilities. | The appointed person or persons have full responsibility for ensuring that the organisation's assets deliver the requirements of the asset management strategy, objectives and plan(s). They have been given the necessary authority to achieve this. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
40 | Structure, authority and responsibilities | What evidence can the organisation's top management provide to demonstrate that sufficient resources are available for asset management? | 2.5 | Orion now has an Asset Management Improvement Plan in place. This document acknowledges that additional roles are required within the AM team. This is being addressed. Unfilled key positions within the AM Team and acknowledged capacity constraints affect organisational structure effectiveness. The challenge in maintaining core AM process improvement momentum while managing CPP workload indicates structural capacity limitations under current demand. A restructured system requiring operational validation appropriately scores at "Competent" threshold pending demonstrated effectiveness under normal business conditions. Orion's restructure in early 2025 is the foundation of the resources Orion needs for their asset management activities as they improve on their journey. However, the current structure may potentially need new roles. For example, they currently do not have any reliability engineers in the organisation. The AMIP will support the development of a process to assess future resource needs, but it is still in a draft state. |  | Optimal asset management requires top management to ensure sufficient resources are available. In this context the term 'resources' includes manpower, materials, funding and service provider support. | Top management. The management team that has overall responsibility for asset management. Risk management team. The organisation's managers involved in day-to-day supervision of asset-related activities, such as frontline managers, engineers, foremen and chargehands as appropriate. | Evidence demonstrating that asset management plan(s) and/or the process(es) for asset management plan implementation consider the provision of adequate resources in both the short and long term. Resources include funding, materials, equipment, services provided by third parties and personnel (internal and service providers) with appropriate skills competencies and knowledge. | 40 | Structure, authority and responsibilities | What evidence can the organisation's top management provide to demonstrate that sufficient resources are available for asset management? | The organisation's top management has not considered the resources required to deliver asset management. | The organisations top management understands the need for sufficient resources but there are no effective mechanisms in place to ensure this is the case. | A process exists for determining what resources are required for its asset management activities and in most cases these are available but in some instances resources remain insufficient. | An effective process exists for determining the resources needed for asset management and sufficient resources are available. It can be demonstrated that resources are matched to asset management requirements. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
42 | Structure, authority and responsibilities | To what degree does the organisation's top management communicate the importance of meeting its asset management requirements? | 3 | Orion undertakes regulate communications both internally and externally to ensure all affect parties are aware of the content of the latest AMPs. E.g. Internally - Staff meetings, asset class focus group meetings. Externally - Customer Advisory Panel, “Powerful Conversations” workshops |  | Widely used AM practice standards require an organisation to communicate the importance of meeting its asset management requirements such that personnel fully understand, take ownership of, and are fully engaged in the delivery of the asset management requirements (eg, PAS 55 s 4.4.1 g). | Top management. The management team that has overall responsibility for asset management. People involved in the delivery of the asset management requirements. | Evidence of such activities as road shows, written bulletins, workshops, team talks and management walk-abouts would assist an organisation to demonstrate it is meeting this requirement of PAS 55. | 42 | Structure, authority and responsibilities | To what degree does the organisation's top management communicate the importance of meeting its asset management requirements? | The organisation's top management has not considered the need to communicate the importance of meeting asset management requirements. | The organisations top management understands the need to communicate the importance of meeting its asset management requirements but does not do so. | Top management communicates the importance of meeting its asset management requirements but only to parts of the organisation. | Top management communicates the importance of meeting its asset management requirements to all relevant parts of the organisation. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
45 | Outsourcing of asset management activities | Where the organisation has outsourced some of its asset management activities, how has it ensured that appropriate controls are in place to ensure the compliant delivery of its organisational strategic plan, and its asset management policy and strategy? | 2.5 | In the past year Orion has made a change to the way they have structured their outsourcing model with their key service delivery partners. They now have a relationship with the “Tight Five” contractors, with Connetics being their designated Primary Service Delivery Partner (PSDP) and the other four contracted companies designated as Service Delivery Partner (SDP). Orion’s Procurement team maintains the contract and service level measures for the “Tight Five”. Orion’s Network Delivery team is responsible for the works programming and delivery of their annual work plan, supported as appropriate by their other teams. The new work flow processes need time to bed in and mature. The model has not been tested against CPP-scale delivery volumes, supporting cautious scoring pending operational validation. Orion have made changes to the way they have structured their outsourcing model, and have continued to focus on improving their relationship with their key contractors, they have not yet implemented controls systematically into the asset management system to ensure outsourced activities are delivered in compliance with the organisational strategy, AM Policy or SAMP. For example, their service delivery partners operate under Master Service Agreements; the conditions (controls) for these contracts are adopted from NZS 3910:2023. While elements of alignment exists, controls are not fully aligned to their organisational strategy, AM Policy or SAMP. |  | Where an organisation chooses to outsource some of its asset management activities, the organisation must ensure that these outsourced process(es) are under appropriate control to ensure that all the requirements of widely used AM standards (eg, PAS 55) are in place, and the asset management policy, strategy objectives and plan(s) are delivered. This includes ensuring capabilities and resources across a time span aligned to life cycle management. The organisation must put arrangements in place to control the outsourced activities, whether it be to external providers or to other in-house departments. This question explores what the organisation does in this regard. | Top management. The management team that has overall responsibility for asset management. The manager(s) responsible for the monitoring and management of the outsourced activities. People involved with the procurement of outsourced activities. The people within the organisations that are performing the outsourced activities. The people impacted by the outsourced activity. | The organisation's arrangements that detail the compliance required of the outsourced activities. For example, this this could form part of a contract or service level agreement between the organisation and the suppliers of its outsourced activities. Evidence that the organisation has demonstrated to itself that it has assurance of compliance of outsourced activities. | 45 | Outsourcing of asset management activities | Where the organisation has outsourced some of its asset management activities, how has it ensured that appropriate controls are in place to ensure the compliant delivery of its organisational strategic plan, and its asset management policy and strategy? | The organisation has not considered the need to put controls in place. | The organisation controls its outsourced activities on an ad-hoc basis, with little regard for ensuring for the compliant delivery of the organisational strategic plan and/or its asset management policy and strategy. | Controls systematically considered but currently only provide for the compliant delivery of some, but not all, aspects of the organisational strategic plan and/or its asset management policy and strategy. Gaps exist. | Evidence exists to demonstrate that outsourced activities are appropriately controlled to provide for the compliant delivery of the organisational strategic plan, asset management policy and strategy, and that these controls are integrated into the asset management system | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
48 | Training, awareness and competence | How does the organisation develop plan(s) for the human resources required to undertake asset management activities - including the development and delivery of asset management strategy, process(es), objectives and plan(s)? | 3.5 | The AMP section 4.2 Planning for changing workforce needs, provides good insights into Orion's future training focuses. Their workforce plan focuses on developing and embedding key processes and systems, and creating an environment for our current and future workforce to thrive by 2028. |  | There is a need for an organisation to demonstrate that it has considered what resources are required to develop and implement its asset management system. There is also a need for the organisation to demonstrate that it has assessed what development plan(s) are required to provide its human resources with the skills and competencies to develop and implement its asset management systems. The timescales over which the plan(s) are relevant should be commensurate with the planning horizons within the asset management strategy considers e.g. if the asset management strategy considers 5, 10 and 15 year time scales then the human resources development plan(s) should align with these. Resources include both 'in house' and external resources who undertake asset management activities. | Senior management responsible for agreement of plan(s). Managers responsible for developing asset management strategy and plan(s). Managers with responsibility for development and recruitment of staff (including HR functions). Staff responsible for training. Procurement officers. Contracted service providers. | Evidence of analysis of future work load plan(s) in terms of human resources. Document(s) containing analysis of the organisation's own direct resources and contractors resource capability over suitable timescales. Evidence, such as minutes of meetings, that suitable management forums are monitoring human resource development plan(s). Training plan(s), personal development plan(s), contract and service level agreements. | 48 | Training, awareness and competence | How does the organisation develop plan(s) for the human resources required to undertake asset management activities - including the development and delivery of asset management strategy, process(es), objectives and plan(s)? | The organisation has not recognised the need for assessing human resources requirements to develop and implement its asset management system. | The organisation has recognised the need to assess its human resources requirements and to develop a plan(s). There is limited recognition of the need to align these with the development and implementation of its asset management system. | The organisation has developed a strategic approach to aligning competencies and human resources to the asset management system including the asset management plan but the work is incomplete or has not been consistently implemented. | The organisation can demonstrate that plan(s) are in place and effective in matching competencies and capabilities to the asset management system including the plan for both internal and contracted activities. Plans are reviewed integral to asset management system process(es). | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
49 | Training, awareness and competence | How does the organisation identify competency requirements and then plan, provide and record the training necessary to achieve the competencies? | 3.5 | Competencies of all personnel working on the Orion network is managed by the training Team and updates are uploaded into the PowerOn system. The PowerOn system holds staff and contractors network competency information. Without the correct competencies, work management permits are not issued if competences are not up to date. Orion's training systems and competency management processes ensures that all people working on their network assets are fully competent and appropriately skilled. Orion has well-developed processes to manage the competencies of all personnel (service providers and Orion operators) who work on the physical network. They also have clear competency requirements for operators, and have developed a competency pathway to ensure career and skill progression. However, there are no structured training requirements or processes for general employees - these are at the discretion of the employee and their manager. They have implemented LinkedIn Learning to allow for additional upskilling and cross-training, but no formal learning requirements are in place. |  | Widely used AM standards require that organisations to undertake a systematic identification of the asset management awareness and competencies required at each level and function within the organisation. Once identified the training required to provide the necessary competencies should be planned for delivery in a timely and systematic way. Any training provided must be recorded and maintained in a suitable format. Where an organisation has contracted service providers in place then it should have a means to demonstrate that this requirement is being met for their employees. (eg, PAS 55 refers to frameworks suitable for identifying competency requirements). | Senior management responsible for agreement of plan(s). Managers responsible for developing asset management strategy and plan(s). Managers with responsibility for development and recruitment of staff (including HR functions). Staff responsible for training. Procurement officers. Contracted service providers. | Evidence of an established and applied competency requirements assessment process and plan(s) in place to deliver the required training. Evidence that the training programme is part of a wider, co-ordinated asset management activities training and competency programme. Evidence that training activities are recorded and that records are readily available (for both direct and contracted service provider staff) e.g. via organisation wide information system or local records database. | 49 | Training, awareness and competence | How does the organisation identify competency requirements and then plan, provide and record the training necessary to achieve the competencies? | The organisation does not have any means in place to identify competency requirements. | The organisation has recognised the need to identify competency requirements and then plan, provide and record the training necessary to achieve the competencies. | The organisation is the process of identifying competency requirements aligned to the asset management plan(s) and then plan, provide and record appropriate training. It is incomplete or inconsistently applied. | Competency requirements are in place and aligned with asset management plan(s). Plans are in place and effective in providing the training necessary to achieve the competencies. A structured means of recording the competencies achieved is in place. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
50 | Training, awareness and competence | How does the organization ensure that persons under its direct control undertaking asset management related activities have an appropriate level of competence in terms of education, training or experience? | 2.5 | Orion continues to strengthen their Talent Programs by ensuring depth in their succession plans and enabling talent mobility via development and growth of their people. Roles have not been formally mapped against a matrix of training and competency requirements. There are internal training courses (Network Access competencies) required to work on specific aspects of the network (HV, LV, Underground, Above ground) and practical training on operating assets but there are some inconsistencies in course content, quality and delivery and a lack of formal training matrix to capture ALL training required and monitor records/ refreshers. Leadership development training is not currently being delivered. |  | A critical success factor for the effective development and implementation of an asset management system is the competence of persons undertaking these activities. organisations should have effective means in place for ensuring the competence of employees to carry out their designated asset management function(s). Where an organisation has contracted service providers undertaking elements of its asset management system then the organisation shall assure itself that the outsourced service provider also has suitable arrangements in place to manage the competencies of its employees. The organisation should ensure that the individual and corporate competencies it requires are in place and actively monitor, develop and maintain an appropriate balance of these competencies. | Managers, supervisors, persons responsible for developing training programmes. Staff responsible for procurement and service agreements. HR staff and those responsible for recruitment. | Evidence of a competency assessment framework that aligns with established frameworks such as the asset management Competencies Requirements Framework (Version 2.0); National Occupational Standards for Management and Leadership; UK Standard for Professional Engineering Competence, Engineering Council, 2005. | 50 | Training, awareness and competence | How does the organization ensure that persons under its direct control undertaking asset management related activities have an appropriate level of competence in terms of education, training or experience? | The organization has not recognised the need to assess the competence of person(s) undertaking asset management related activities. | Competency of staff undertaking asset management related activities is not managed or assessed in a structured way, other than formal requirements for legal compliance and safety management. | The organization is in the process of putting in place a means for assessing the competence of person(s) involved in asset management activities including contractors. There are gaps and inconsistencies. | Competency requirements are identified and assessed for all persons carrying out asset management related activities - internal and contracted. Requirements are reviewed and staff reassessed at appropriate intervals aligned to asset management requirements. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
53 | Communication, participation and consultation | How does the organisation ensure that pertinent asset management information is effectively communicated to and from employees and other stakeholders, including contracted service providers? | 2.5 | Overall Orion is a good communicator and has many processes in place for both internal and external communications. As a community owned organisation, their focus is always on the communities they serve. The following are a few references from the AMP 2024: 3.2 Stakeholder interests: 3.3.1 Customer Advisory Panel 3.3.2 Customer satisfaction research 3.3.3 “Powerful Conversations” workshops Orion see opportunities to improve how they have two-way communication between all relevant parties. For example, currently: - They don't provide the information service delivery partners need in AMP, e.g., quantity of increase - AMP info is not effectively communicated to match the requirements of asset management strategy, plan(s) and process(es) to customers. To close this gap, they are developing a forward works viewer for their service delivery partners, to help them understand Orion's anticipated programme of work and resource appropriately. |  | Widely used AM practice standards require that pertinent asset management information is effectively communicated to and from employees and other stakeholders including contracted service providers. Pertinent information refers to information required in order to effectively and efficiently comply with and deliver asset management strategy, plan(s) and objectives. This will include for example the communication of the asset management policy, asset performance information, and planning information as appropriate to contractors. | Top management and senior management representative(s), employee's representative(s), employee's trade union representative(s); contracted service provider management and employee representative(s); representative(s) from the organisation's Health, Safety and Environmental team. Key stakeholder representative(s). | Asset management policy statement prominently displayed on notice boards, intranet and internet; use of organisation's website for displaying asset performance data; evidence of formal briefings to employees, stakeholders and contracted service providers; evidence of inclusion of asset management issues in team meetings and contracted service provider contract meetings; newsletters, etc. | 53 | Communication, participation and consultation | How does the organisation ensure that pertinent asset management information is effectively communicated to and from employees and other stakeholders, including contracted service providers? | The organisation has not recognised the need to formally communicate any asset management information. | There is evidence that the pertinent asset management information to be shared along with those to share it with is being determined. | The organisation has determined pertinent information and relevant parties. Some effective two way communication is in place but as yet not all relevant parties are clear on their roles and responsibilities with respect to asset management information. | Two way communication is in place between all relevant parties, ensuring that information is effectively communicated to match the requirements of asset management strategy, plan(s) and process(es). Pertinent asset information requirements are regularly reviewed. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
59 | Asset Management System documentation | What documentation has the organisation established to describe the main elements of its asset management system and interactions between them? | 2 | Orion has detailed asset management documents which are constantly being updated to stay up with new development initiatives. The Orion AMP 2024 – section 2.6 Asset Management Framework, onwards, provides extensive details on how the asset management system exists to ensure all assets within the Orion network are appropriately managed. SAMP is referenced for more up to date information given it's the latest work and has been peer reviewed. Variable documentation maturity across the asset management system prevents higher scoring. Orion are in the process of establishing documentation that comprehensively describes all of the main elements of their AM System and the interactions between them. |  | Widely used AM practice standards require an organisation maintain up to date documentation that ensures that its asset management systems (ie, the systems the organisation has in place to meet the standards) can be understood, communicated and operated. (eg, s 4.5 of PAS 55 requires the maintenance of up to date documentation of the asset management system requirements specified throughout s 4 of PAS 55). | The management team that has overall responsibility for asset management. Managers engaged in asset management activities. | The documented information describing the main elements of the asset management system (process(es)) and their interaction. | 59 | Asset Management System documentation | What documentation has the organisation established to describe the main elements of its asset management system and interactions between them? | The organisation has not established documentation that describes the main elements of the asset management system. | The organisation is aware of the need to put documentation in place and is in the process of determining how to document the main elements of its asset management system. | The organisation in the process of documenting its asset management system and has documentation in place that describes some, but not all, of the main elements of its asset management system and their interaction. | The organisation has established documentation that comprehensively describes all the main elements of its asset management system and the interactions between them. The documentation is kept up to date. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
62 | Information management | What has the organisation done to determine what its asset management information system(s) should contain in order to support its asset management system? | 2 | Orion is transforming their operating model to become an increasingly digital business, modernising their core platforms and leveraging digital services, automation and data intelligence to drive business performance and improve customer outcomes. Edison notes that the selection of the IBM Maximo application for the CMMS function is an extremely good move. Maximo is a long-standing asset management focused tool used by many high achieving infrastructure organizations Many of the key asset management related systems are currently being implemented so it will be a couple of years before these are fully While Orion are transforming their operating model to become an increasingly digital business, they are still in the process of implementing Maximo and ESRI. They have not yet developed requirements relating to the whole life cycle and cover information originating from both internal and external sources for all asset fleets. |  | Effective asset management requires appropriate information to be available. Widely used AM standards therefore require the organisation to identify the asset management information it requires in order to support its asset management system. Some of the information required may be held by suppliers. The maintenance and development of asset management information systems is a poorly understood specialist activity that is akin to IT management but different from IT management. This group of questions provides some indications as to whether the capability is available and applied. Note: To be effective, an asset information management system requires the mobilisation of technology, people and process(es) that create, secure, make available and destroy the information required to support the asset management system. | The organisation's strategic planning team. The management team that has overall responsibility for asset management. Information management team. Operations, maintenance and engineering managers | Details of the process the organisation has employed to determine what its asset information system should contain in order to support its asset management system. Evidence that this has been effectively implemented. | 62 | Information management | What has the organisation done to determine what its asset management information system(s) should contain in order to support its asset management system? | The organisation has not considered what asset management information is required. | The organisation is aware of the need to determine in a structured manner what its asset information system should contain in order to support its asset management system and is in the process of deciding how to do this. | The organisation has developed a structured process to determine what its asset information system should contain in order to support its asset management system and has commenced implementation of the process. | The organisation has determined what its asset information system should contain in order to support its asset management system. The requirements relate to the whole life cycle and cover information originating from both internal and external sources. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
63 | Information management | How does the organisation maintain its asset management information system(s) and ensure that the data held within it (them) is of the requisite quality and accuracy and is consistent? | 2 | Orion is transforming their operating model to become an increasingly digital business, modernising their core platforms and leveraging digital services, automation and data intelligence to drive business performance and improve customer outcomes. They are in the process of developing effective controls for all asset fleets. Maximo, when fully implemented, will assist with this consistency and ensure that controls are regularly reviewed and improved where necessary. Orion have areas of strength, but they do not have consistent evidence of "effective" controls that are regularly reviewed and improved across all asset fleets, where necessary. |  | The response to the questions is progressive. A higher scale cannot be awarded without achieving the requirements of the lower scale. This question explores how the organisation ensures that information management meets widely used AM practice requirements (eg, s 4.4.6 (a), (c) and (d) of PAS 55). | The management team that has overall responsibility for asset management. Users of the organisational information systems. | The asset management information system, together with the policies, procedure(s), improvement initiatives and audits regarding information controls. | 63 | Information management | How does the organisation maintain its asset management information system(s) and ensure that the data held within it (them) is of the requisite quality and accuracy and is consistent? | There are no formal controls in place or controls are extremely limited in scope and/or effectiveness. | The organisation is aware of the need for effective controls and is in the process of developing an appropriate control process(es). | The organisation has developed a controls that will ensure the data held is of the requisite quality and accuracy and is consistent and is in the process of implementing them. | The organisation has effective controls in place that ensure the data held is of the requisite quality and accuracy and is consistent. The controls are regularly reviewed and improved where necessary. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
64 | Information management | How has the organisation's ensured its asset management information system is relevant to its needs? | 2 | Many of Orion’s current systems supporting their asset management processes are end of life. Their goal is to modernise the systems supporting the management of their network and uplift their asset management capabilities. It is noted that the selection of the IBM Maximo application for the CMMS function is an extremely good move. Maximo is a long-standing asset management focused tool used by many high achieving infrastructure organizations. Orion are in the process of implementing a process to ensure their asset management information system is relevant to their needs by implementing Maximo. Until this is completed, many of their asset management information systems are at end of life (as outlined in their 2024 AMP), and there are gaps between what the information systems provide and what their organisation needs. |  | Widely used AM standards need not be prescriptive about the form of the asset management information system, but simply require that the asset management information system is appropriate to the organisations needs, can be effectively used and can supply information which is consistent and of the requisite quality and accuracy. | The organisation's strategic planning team. The management team that has overall responsibility for asset management. Information management team. Users of the organisational information systems. | The documented process the organisation employs to ensure its asset management information system aligns with its asset management requirements. Minutes of information systems review meetings involving users. | 64 | Information management | How has the organisation's ensured its asset management information system is relevant to its needs? | The organisation has not considered the need to determine the relevance of its management information system. At present there are major gaps between what the information system provides and the organisations needs. | The organisation understands the need to ensure its asset management information system is relevant to its needs and is determining an appropriate means by which it will achieve this. At present there are significant gaps between what the information system provides and the organisations needs. | The organisation has developed and is implementing a process to ensure its asset management information system is relevant to its needs. Gaps between what the information system provides and the organisations needs have been identified and action is being taken to close them. | The organisation's asset management information system aligns with its asset management requirements. Users can confirm that it is relevant to their needs. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
69 | Risk management process(es) | How has the organisation documented process(es) and/or procedure(s) for the identification and assessment of asset and asset management related risks throughout the asset life cycle? | 2.5 | Due to the nature of Orion’s business, risk management is a key focus in everything they do. They are currently further developing their Enterprise Risk Management (ERM) processes and systems. We have previously noted Enterprise Risk Management (ERM) framework development aligned to ISO 31000 principles, and that "A large amount of improvement work is currently being undertaken in the ERM. These processes and integrations need time to mature to see how they perform and deliver benefits to the business. Orion are stronger in some asset fleets and asset lifecycle stages than others. For example, identification and assessment of asset related risk across the asset lifecycle is done but not fully documented. They document some in ACS, business cases and PODs, however, they are not consistently applied across all lifecycle phases, e.g., maintenance, procurement, delivery and etc. |  | Risk management is an important foundation for proactive asset management. Its overall purpose is to understand the cause, effect and likelihood of adverse events occurring, to optimally manage such risks to an acceptable level, and to provide an audit trail for the management of risks. Widely used standards require the organisation to have process(es) and/or procedure(s) in place that set out how the organisation identifies and assesses asset and asset management related risks. The risks have to be considered across the four phases of the asset lifecycle (eg, para 4.3.3 of PAS 55). | The top management team in conjunction with the organisation's senior risk management representatives. There may also be input from the organisation's Safety, Health and Environment team. Staff who carry out risk identification and assessment. | The organisation's risk management framework and/or evidence of specific process(es) and/ or procedure(s) that deal with risk control mechanisms. Evidence that the process(es) and/or procedure(s) are implemented across the business and maintained. Evidence of agendas and minutes from risk management meetings. Evidence of feedback in to process(es) and/or procedure(s) as a result of incident investigation(s). Risk registers and assessments. | 69 | Risk management process(es) | How has the organisation documented process(es) and/or procedure(s) for the identification and assessment of asset and asset management related risks throughout the asset life cycle? | The organisation has not considered the need to document process(es) and/or procedure(s) for the identification and assessment of asset and asset management related risks throughout the asset life cycle. | The organisation is aware of the need to document the management of asset related risk across the asset lifecycle. The organisation has plan(s) to formally document all relevant process(es) and procedure(s) or has already commenced this activity. | The organisation is in the process of documenting the identification and assessment of asset related risk across the asset lifecycle but it is incomplete or there are inconsistencies between approaches and a lack of integration. | Identification and assessment of asset related risk across the asset lifecycle is fully documented. The organisation can demonstrate that appropriate documented mechanisms are integrated across life cycle phases and are being consistently applied. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
79 | Use and maintenance of asset risk information | How does the organisation ensure that the results of risk assessments provide input into the identification of adequate resources and training and competency needs? | 2 | Operational key risks have been identified. Risk information is a key asset decision making tool and is being improved as the new Enterprise Risk Management process is improved and developed. We have previously noted Asset Health and Criticality measures are used "to varying degrees on various asset classes" and that "More work is intended to be done on these measures to help gain more awareness of their benefits." While significant CPP investment is substantially justified by failure risks posed by ageing assets, the ability to effectively use and maintain asset risk information is currently constrained by incomplete systems and acknowledged legacy data limitations. The area is "undergoing a huge amount of improvement." Inconsistent application across asset classes, acknowledged need for enhanced understanding of risk measures, and explicit improvement requirements indicate this capability is developing rather than systematically embedded. Orion's approach to risk assessments feeding into standards/procedures and subsequently training and monitoring activity is not formally mapped and inconsistently applied. There is no central location for risk assessments to be stored and no system to map that these or any controls identified have been captured in new designs/ specifications. The audit process to verify standards are being applied correctly is ad hoc and there is no formal reporting mechanism to demonstrate these are done or corrective actions/ risk reduction activities are being undertaken. Orion do risk assessments, but they don't see a specific link between a risk assessment and a standard change, and the standard change officially happening - no document/change management; they sometimes have a risk assessment and do nothing from it - need to have a mechanism to have risk assessment feed into change (i.e. investigate if change is possible, then move into doing it). |  | Widely used AM standards require that the output from risk assessments are considered and that adequate resource (including staff) and training is identified to match the requirements. It is a further requirement that the effects of the control measures are considered, as there may be implications in resources and training required to achieve other objectives. | Staff responsible for risk assessment and those responsible for developing and approving resource and training plan(s). There may also be input from the organisation's Safety, Health and Environment team. | The organisations risk management framework. The organisation's resourcing plan(s) and training and competency plan(s). The organisation should be able to demonstrate appropriate linkages between the content of resource plan(s) and training and competency plan(s) to the risk assessments and risk control measures that have been developed. | 79 | Use and maintenance of asset risk information | How does the organisation ensure that the results of risk assessments provide input into the identification of adequate resources and training and competency needs? | The organisation has not considered the need to conduct risk assessments. | The organisation is aware of the need to consider the results of risk assessments and effects of risk control measures to provide input into reviews of resources, training and competency needs. Current input is typically ad-hoc and reactive. | The organisation is in the process ensuring that outputs of risk assessment are included in developing requirements for resources and training. The implementation is incomplete and there are gaps and inconsistencies. | Outputs from risk assessments are consistently and systematically used as inputs to develop resources, training and competency requirements. Examples and evidence is available. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
82 | Legal and other requirements | What procedure does the organisation have to identify and provide access to its legal, regulatory, statutory and other asset management requirements, and how is requirements incorporated into the asset management system? | 2 | Orion currently use an external consultancy to monitor and report on regulatory, and compliance matters so that they can ensure active compliance within the whole of their business. They are aware that there are currently many new statutory requirements being forced onto their industry. They actively provide submissions during consultation period for many of these process reviews by government agencies. They have procedures to identify legal, regulatory, statutory and other asset management requirements, including external consultancy for regulatory monitoring, active participation in government consultation processes, and established relationships with third-party advisors for financial and technical compliance. However, their approach is not adequately systematic or consistently managed across the organisation. For example, while their Engineering Standards contain requirements they must meet, they lack explicit linkages to the underlying legal and regulatory sources (e.g. Transpower, Electricity Industry Participation Code 2010, NZ/AUS Engineering Standards), making it difficult to demonstrate why specific requirements exist and how they connect back to Orion's statutory obligations. Orion's information management is fragmented; they have no integrated view or holistic reporting system to track their compliance positioning across Orion. They rely heavily on SME knowledge and external advisors, rather than systematic controls and documented processes, with no formal mechanism to track and monitor changing requirements beyond individual monitoring and internal education. Orion's AM information system (Maximo) does not yet have the systematic processes needed to store and report on compliance requirements against assets. These gaps mean their requirements are inconsistently managed, despite having foundational procedures in place. They are evaluating the use of a compliance software (e.g. Comply With) to provide a holistic overview and reporting mechanism. |  | In order for an organisation to comply with its legal, regulatory, statutory and other asset management requirements, the organisation first needs to ensure that it knows what they are (eg, PAS 55 specifies this in s 4.4.8). It is necessary to have systematic and auditable mechanisms in place to identify new and changing requirements. Widely used AM standards also require that requirements are incorporated into the asset management system (e.g. procedure(s) and process(es)) | Top management. The organisations regulatory team. The organisation's legal team or advisors. The management team with overall responsibility for the asset management system. The organisation's health and safety team or advisors. The organisation's policy making team. | The organisational processes and procedures for ensuring information of this type is identified, made accessible to those requiring the information and is incorporated into asset management strategy and objectives | 82 | Legal and other requirements | What procedure does the organisation have to identify and provide access to its legal, regulatory, statutory and other asset management requirements, and how is requirements incorporated into the asset management system? | The organisation has not considered the need to identify its legal, regulatory, statutory and other asset management requirements. | The organisation identifies some its legal, regulatory, statutory and other asset management requirements, but this is done in an ad-hoc manner in the absence of a procedure. | The organisation has procedure(s) to identify its legal, regulatory, statutory and other asset management requirements, but the information is not kept up to date, inadequate or inconsistently managed. | Evidence exists to demonstrate that the organisation's legal, regulatory, statutory and other asset management requirements are identified and kept up to date. Systematic mechanisms for identifying relevant legal and statutory requirements. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
88 | Life Cycle Activities | How does the organisation establish implement and maintain process(es) for the implementation of its asset management plan(s) and control of activities across the creation, acquisition or enhancement of assets. This includes design, modification, procurement, construction and commissioning activities? | 2 | With the creation of new roles within the Asset Management Team, Asset Class Strategy documents have recently been created or are being created to look at everything relating to the asset class, including asset lifecycle management, maintenance, renewals and continuous improvement. Orion are in the process of implementing or improving processes and procedures to manage and control the implementation of their AMP. For example, while they have a process to show how a project is implemented, they do not have evidence to show the process is effective. |  | Life cycle activities are about the implementation of asset management plan(s) i.e. they are the "doing" phase. They need to be done effectively and well in order for asset management to have any practical meaning. As a consequence, widely used standards (eg, PAS 55 s 4.5.1) require organisations to have in place appropriate process(es) and procedure(s) for the implementation of asset management plan(s) and control of lifecycle activities. This question explores those aspects relevant to asset creation. | Asset managers, design staff, construction staff and project managers from other impacted areas of the business, e.g. Procurement | Documented process(es) and procedure(s) which are relevant to demonstrating the effective management and control of life cycle activities during asset creation, acquisition, enhancement including design, modification, procurement, construction and commissioning. | 88 | Life Cycle Activities | How does the organisation establish implement and maintain process(es) for the implementation of its asset management plan(s) and control of activities across the creation, acquisition or enhancement of assets. This includes design, modification, procurement, construction and commissioning activities? | The organisation does not have process(es) in place to manage and control the implementation of asset management plan(s) during activities related to asset creation including design, modification, procurement, construction and commissioning. | The organisation is aware of the need to have process(es) and procedure(s) in place to manage and control the implementation of asset management plan(s) during activities related to asset creation including design, modification, procurement, construction and commissioning but currently do not have these in place (note: procedure(s) may exist but they are inconsistent/incomplete). | The organisation is in the process of putting in place process(es) and procedure(s) to manage and control the implementation of asset management plan(s) during activities related to asset creation including design, modification, procurement, construction and commissioning. Gaps and inconsistencies are being addressed. | Effective process(es) and procedure(s) are in place to manage and control the implementation of asset management plan(s) during activities related to asset creation including design, modification, procurement, construction and commissioning. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
91 | Life Cycle Activities | How does the organisation ensure that process(es) and/or procedure(s) for the implementation of asset management plan(s) and control of activities during maintenance (and inspection) of assets are sufficient to ensure activities are carried out under specified conditions, are consistent with asset management strategy and control cost, risk and performance? | 2 | Orion's new Asset Management team has developed a whole new group of strategic documents for all of their main asset classes. These cover the whole life cycle of the asset and everything to do with that asset. We have previously noted Asset Class Strategy documents have been recently created or are in development. Past deferral of asset renewal activities during the post-earthquake recovery period has been noted. This historical deferred maintenance accumulation indicates past lifecycle management did not prevent asset deterioration. New strategies have not been tested through complete asset lifecycle implementation cycles, and effectiveness relies substantially on accurate Maximo Job Plan implementation. The accumulation of deferred maintenance necessitating additional future funding mechanisms indicates historical lifecycle management did not prevent asset deterioration. Orion do not carry out preventative (inspections, etc) and corrective (triage/prioritisation) consistently on all asset fleets. While they have pockets of excellence, such as their renewals, some areas are being discussed as part of their CPP application and IAM implementation. |  | Having documented process(es) which ensure the asset management plan(s) are implemented in accordance with any specified conditions, in a manner consistent with the asset management policy, strategy and objectives and in such a way that cost, risk and asset system performance are appropriately controlled is critical. They are an essential part of turning intention into action (eg, as required by PAS 55 s 4.5.1). | Asset managers, operations managers, maintenance managers and project managers from other impacted areas of the business | Documented procedure for review. Documented procedure for audit of process delivery. Records of previous audits, improvement actions and documented confirmation that actions have been carried out. | 91 | Life Cycle Activities | How does the organisation ensure that process(es) and/or procedure(s) for the implementation of asset management plan(s) and control of activities during maintenance (and inspection) of assets are sufficient to ensure activities are carried out under specified conditions, are consistent with asset management strategy and control cost, risk and performance? | The organisation does not have process(es)/procedure(s) in place to control or manage the implementation of asset management plan(s) during this life cycle phase. | The organisation is aware of the need to have process(es) and procedure(s) in place to manage and control the implementation of asset management plan(s) during this life cycle phase but currently do not have these in place and/or there is no mechanism for confirming they are effective and where needed modifying them. | The organisation is in the process of putting in place process(es) and procedure(s) to manage and control the implementation of asset management plan(s) during this life cycle phase. They include a process for confirming the process(es)/procedure(s) are effective and if necessary carrying out modifications. | The organisation has in place process(es) and procedure(s) to manage and control the implementation of asset management plan(s) during this life cycle phase. They include a process, which is itself regularly reviewed to ensure it is effective, for confirming the process(es)/ procedure(s) are effective and if necessary carrying out modifications. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
95 | Performance and condition monitoring | How does the organisation measure the performance and condition of its assets? | 2 | Orion is currently developing a sweet of new systems to replace outdated legacy systems used to collect and manage asset performance and condition monitoring data. They intend to continue to collect the best possible up to date data, ensure it’s quality and make all data available within one data storage source. As more new systems are integrated with each other and share timely clean data, Orion aims to make a step change in it’s asset management performance and condition monitoring outputs. This is intended to improve asset management decision making. Orion has traditional collected a lot of asset data, but they are now clear that some of this historic data is not as sound and accurate as it could be, so they are planning to improve these situations over the next few years. We have previously acknowledged plans to replace outdated legacy systems with new platforms (Maximo, GIS). Our assessment has assessment explicitly noted "some data is not of high quality currently, but plans are in place to improve these data sets as new systems are implemented" and that "historic data is not as sound and accurate as it could be." The CPP application is predicated on achieving a "step change" in decision-making through new systems, indicating current monitoring systems require enhancement. Acknowledged current data quality limitations affect performance and condition monitoring effectiveness. Plans for future improvement do not constitute current capability. The necessity to implement comprehensive new systems to achieve adequate monitoring capability indicates current state is at a level 2 scoring currently. Orion are stronger in some asset fleets (especially those that support our 11kV+ network), than others. For example, on their LV network, they are just starting to get more visibility into our network; they are not yet conducting consistent asset performance monitoring and consistent approaches across this fleet. Until Maximo is implemented, they do not yet meet the criteria for level 3. |  | Widely used AM standards require that organisations establish implement and maintain procedure(s) to monitor and measure the performance and/or condition of assets and asset systems. They further set out requirements in some detail for reactive and proactive monitoring, and leading/lagging performance indicators together with the monitoring or results to provide input to corrective actions and continual improvement. There is an expectation that performance and condition monitoring will provide input to improving asset management strategy, objectives and plan(s). | A broad cross-section of the people involved in the organisation's asset-related activities from data input to decision-makers, i.e. an end-to end assessment. This should include contactors and other relevant third parties as appropriate. | Functional policy and/or strategy documents for performance or condition monitoring and measurement. The organisation's performance monitoring frameworks, balanced scorecards etc. Evidence of the reviews of any appropriate performance indicators and the action lists resulting from these reviews. Reports and trend analysis using performance and condition information. Evidence of the use of performance and condition information shaping improvements and supporting asset management strategy, objectives and plan(s). | 95 | Performance and condition monitoring | How does the organisation measure the performance and condition of its assets? | The organisation has not considered how to monitor the performance and condition of its assets. | The organisation recognises the need for monitoring asset performance but has not developed a coherent approach. Measures are incomplete, predominantly reactive and lagging. There is no linkage to asset management objectives. | The organisation is developing coherent asset performance monitoring linked to asset management objectives. Reactive and proactive measures are in place. Use is being made of leading indicators and analysis. Gaps and inconsistencies remain. | Consistent asset performance monitoring linked to asset management objectives is in place and universally used including reactive and proactive measures. Data quality management and review process are appropriate. Evidence of leading indicators and analysis. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
99 | Investigation of asset-related failures, incidents and nonconformities | How does the organisation ensure responsibility and the authority for the handling, investigation and mitigation of asset-related failures, incidents and emergency situations and non conformances is clear, unambiguous, understood and communicated? | 2 | When an asset failure is reported, a specialist team undertakes the investigation, reporting and improvement processes as required. If required processes will be changed, following a rigorous change management process. Orion have a well established process, responsibility and authority for investigation of incidents that result in zone sub / sub transmission outages which are low in probability. However, they do not apply these across the business consistently. For example, other incidents or asset failures e.g., crossarm or insulators, 11kV distribution assets do not trigger an investigation. |  | Widely used AM standards require that the organisation establishes implements and maintains process(es) for the handling and investigation of failures incidents and non-conformities for assets and sets down a number of expectations. Specifically this question examines the requirement to define clearly responsibilities and authorities for these activities, and communicate these unambiguously to relevant people including external stakeholders if appropriate. | The organisation's safety and environment management team. The team with overall responsibility for the management of the assets. People who have appointed roles within the asset-related investigation procedure, from those who carry out the investigations to senior management who review the recommendations. Operational controllers responsible for managing the asset base under fault conditions and maintaining services to consumers. Contractors and other third parties as appropriate. | Process(es) and procedure(s) for the handling, investigation and mitigation of asset-related failures, incidents and emergency situations and non conformances. Documentation of assigned responsibilities and authority to employees. Job Descriptions, Audit reports. Common communication systems i.e. all Job Descriptions on Internet etc. | 99 | Investigation of asset-related failures, incidents and nonconformities | How does the organisation ensure responsibility and the authority for the handling, investigation and mitigation of asset-related failures, incidents and emergency situations and non conformances is clear, unambiguous, understood and communicated? | The organisation has not considered the need to define the appropriate responsibilities and the authorities. | The organisation understands the requirements and is in the process of determining how to define them. | The organisation are in the process of defining the responsibilities and authorities with evidence. Alternatively there are some gaps or inconsistencies in the identified responsibilities/authorities. | The organisation have defined the appropriate responsibilities and authorities and evidence is available to show that these are applied across the business and kept up to date. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
Question No. | Function | Question | Score | Evidence—Summary | User Guidance | Why | Who | Record/documented Information | Question No. | Function | Question | Maturity Level 0 | Maturity Level 1 | Maturity Level 2 | Maturity Level 3 | Maturity Level 4
105 | Audit | What has the organisation done to establish procedure(s) for the audit of its asset management system (process(es))? | 2 | Business internal audit programme exists and are reported on at high levels of the organisation. Most asset management related activities full within these audits. Asset management processes have their own cycle of review and updates as mentioned earlier in this report. We have noted business internal audit programme exists at senior organisational levels. However, recommendations in the assessment included "More visibility in this area is required," "end-to-end process mapping" should be undertaken using Flowingly, and "more visibility should be available to show how and when audits are undertaken on the asset management system and core processes." The emphasis on ISO 55001 alignment highlights opportunities to enhance audit documentation and visibility. Explicit recommendations for enhanced visibility and systematic process mapping indicate current audit processes provide limited asset management system assurance. While basic audit programmes exist, the systematic, comprehensive AM system auditing required for certification readiness is not yet established. while Orion have an extensive business assurance programme, they cannot demonstrate that their audit procedures cover all appropriate asset-related activities and associated reporting of audit results. For example, various AM related audits took place over the last 3-6 years and there are still a number of action items that have not been closed out. We expect this score to improve in the future as Orion work to implement their AM Improvement Plan and improve their internal audit function capability and scope. |  | This question seeks to explore what the organisation has done to comply with the standard practice AM audit requirements (eg, the associated requirements of PAS 55 s 4.6.4 and its linkages to s 4.7). | The management team responsible for its asset management procedure(s). The team with overall responsibility for the management of the assets. Audit teams, together with key staff responsible for asset management. For example, Asset Management Director, Engineering Director. People with responsibility for carrying out risk assessments | The organisation's asset-related audit procedure(s). The organisation's methodology(s) by which it determined the scope and frequency of the audits and the criteria by which it identified the appropriate audit personnel. Audit schedules, reports etc. Evidence of the procedure(s) by which the audit results are presented, together with any subsequent communications. The risk assessment schedule or risk registers. | 105 | Audit | What has the organisation done to establish procedure(s) for the audit of its asset management system (process(es))? | The organisation has not recognised the need to establish procedure(s) for the audit of its asset management system. | The organisation understands the need for audit procedure(s) and is determining the appropriate scope, frequency and methodology(s). | The organisation is establishing its audit procedure(s) but they do not yet cover all the appropriate asset-related activities. | The organisation can demonstrate that its audit procedure(s) cover all the appropriate asset-related activities and the associated reporting of audit results. Audits are to an appropriate level of detail and consistently managed. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
109 | Corrective & Preventative action | How does the organisation instigate appropriate corrective and/or preventive actions to eliminate or prevent the causes of identified poor performance and non conformance? | 2.5 | All asset classes now have strategy documents which outline the required preventative and corrective actions that are required. With the implementation of the new Maximo and GIS systems, more information and data related to specific asset will be available to staff and contractors. Maximo will allow improved planning and scheduling of preventative maintenance (PM) tasks and also enable collection of more detailed corrective information following work on an asset fault or defect (DM) activities. The reliance on future system implementation for process effectiveness, combined with historical renewal deferrals, indicates current corrective and preventative action processes were insufficient to prevent asset deterioration. Enhanced visibility requirements and pending Maximo-enabled improvements indicate current state is at a "Developing" level requiring systematic enhancement. While Maximo will drive future improvement, they do not yet have mechanisms consistently in place across all asset fleets that are effective for the systematic instigation of P & C actions to address root causes of non-compliance or incidents. Orion's focus has historically been on high-risk activities and assets. Maximo will help them drive improvements in this area, when it is fully implemented. |  | Having investigated asset related failures, incidents and non-conformances, and taken action to mitigate their consequences, an organisation is required to implement preventative and corrective actions to address root causes. Incident and failure investigations are only useful if appropriate actions are taken as a result to assess changes to a businesses risk profile and ensure that appropriate arrangements are in place should a recurrence of the incident happen. Widely used AM standards also require that necessary changes arising from preventive or corrective action are made to the asset management system. | The management team responsible for its asset management procedure(s). The team with overall responsibility for the management of the assets. Audit and incident investigation teams. Staff responsible for planning and managing corrective and preventive actions. | Analysis records, meeting notes and minutes, modification records. Asset management plan(s), investigation reports, audit reports, improvement programmes and projects. Recorded changes to asset management procedure(s) and process(es). Condition and performance reviews. Maintenance reviews | 109 | Corrective & Preventative action | How does the organisation instigate appropriate corrective and/or preventive actions to eliminate or prevent the causes of identified poor performance and non conformance? | The organisation does not recognise the need to have systematic approaches to instigating corrective or preventive actions. | The organisation recognises the need to have systematic approaches to instigating corrective or preventive actions. There is ad-hoc implementation for corrective actions to address failures of assets but not the asset management system. | The need is recognized for systematic instigation of preventive and corrective actions to address root causes of non compliance or incidents identified by investigations, compliance evaluation or audit. It is only partially or inconsistently in place. | Mechanisms are consistently in place and effective for the systematic instigation of preventive and corrective actions to address root causes of non compliance or incidents identified by investigations, compliance evaluation or audit. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
113 | Continual Improvement | How does the organisation achieve continual improvement in the optimal combination of costs, asset related risks and the performance and condition of assets and asset systems across the whole life cycle? | 2.5 | Orion is developing improved systems to ensure they can better manage their continual improvement activities. In the past they have strived for improvements in these areas but have been constrained by outdated systems and poor data collection and quality. We have previously acknowledged Orion demonstrates commitment to asset management enhancement through multiple initiatives. However, the assessment noted Orion "have been constrained by outdated systems and poor data collection and quality," that "documentation maturity remains variable," "Risk quantification and predictive action flagged as areas requiring continued development," and "Improvement roadmap required to align current practices with ISO 55001:2024 requirements." System improvement is only part of the equation and Orion haven't fully implemented it yet. Risk assessment and performance e.g., reliability etc are all areas they need to uplift. |  | Widely used AM standards have requirements to establish, implement and maintain process(es)/procedure(s) for identifying, assessing, prioritising and implementing actions to achieve continual improvement. Specifically there is a requirement to demonstrate continual improvement in optimisation of cost risk and performance/condition of assets across the life cycle. This question explores an organisation's capabilities in this area—looking for systematic improvement mechanisms rather that reviews and audit (which are separately examined). | The top management of the organisation. The manager/team responsible for managing the organisation's asset management system, including its continual improvement. Managers responsible for policy development and implementation. | Records showing systematic exploration of improvement. Evidence of new techniques being explored and implemented. Changes in procedure(s) and process(es) reflecting improved use of optimisation tools/techniques and available information. Evidence of working parties and research. | 113 | Continual Improvement | How does the organisation achieve continual improvement in the optimal combination of costs, asset related risks and the performance and condition of assets and asset systems across the whole life cycle? | The organisation does not consider continual improvement of these factors to be a requirement, or has not considered the issue. | A Continual Improvement ethos is recognised as beneficial, however it has just been started, and or covers partially the asset drivers. | Continuous improvement process(es) are set out and include consideration of cost risk, performance and condition for assets managed across the whole life cycle but it is not yet being systematically applied. | There is evidence to show that continuous improvement process(es) which include consideration of cost risk, performance and condition for assets managed across the whole life cycle are being systematically applied. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.
115 | Continual Improvement | How does the organisation seek and acquire knowledge about new asset management related technology and practices, and evaluate their potential benefit to the organisation? | 3 | Orion is developing improved systems to ensure they can better manage their continual improvement activities. In the past they have strived for improvements in these areas but have been constrained by outdated systems and poor data collection and quality. We have previously acknowledged Orion demonstrates commitment to asset management enhancement through multiple initiatives. However, the assessment noted Orion "have been constrained by outdated systems and poor data collection and quality," that "documentation maturity remains variable, "Risk quantification and predictive action flagged as areas requiring continued development," and "Improvement roadmap required to align current practices with ISO 55001:2024 requirements." System improvement is only part of the equation and Orion haven't fully implemented it yet. Risk assessment and performance e.g., reliability etc are all areas they need to uplift. |  | One important aspect of continual improvement is where an organisation looks beyond its existing boundaries and knowledge base to look at what 'new things are on the market'. These new things can include equipment, process(es), tools, etc. An organisation which does this (eg, by the PAS 55 s 4.6 standards) will be able to demonstrate that it continually seeks to expand its knowledge of all things affecting its asset management approach and capabilities. The organisation will be able to demonstrate that it identifies any such opportunities to improve, evaluates them for suitability to its own organisation and implements them as appropriate. This question explores an organisation's approach to this activity. | The top management of the organisation. The manager/team responsible for managing the organisation's asset management system, including its continual improvement. People who monitor the various items that require monitoring for 'change'. People that implement changes to the organisation's policy, strategy, etc. People within an organisation with responsibility for investigating, evaluating, recommending and implementing new tools and techniques, etc. | Research and development projects and records, benchmarking and participation knowledge exchange professional forums. Evidence of correspondence relating to knowledge acquisition. Examples of change implementation and evaluation of new tools, and techniques linked to asset management strategy and objectives. | 115 | Continual Improvement | How does the organisation seek and acquire knowledge about new asset management related technology and practices, and evaluate their potential benefit to the organisation? | The organisation makes no attempt to seek knowledge about new asset management related technology or practices. | The organisation is inward looking, however it recognises that asset management is not sector specific and other sectors have developed good practice and new ideas that could apply. Ad-hoc approach. | The organisation has initiated asset management communication within sector to share and, or identify 'new' to sector asset management practices and seeks to evaluate them. | The organisation actively engages internally and externally with other asset management practitioners, professional bodies and relevant conferences. Actively investigates and evaluates new practices and evolves its asset management activities using appropriate developments. | The organisation's process(es) surpass the standard required to comply with requirements set out in a recognised standard. The assessor is advised to note in the Evidence section why this is the case and the evidence seen.